## Info
Name | PDTN
Version | 1.1-1-00
Description | PDTN Pressure Transmitter 1.1-1-00

## en
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overview
System
|  |  | Device | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
Pressure Channel 1
|  |  | Pressure | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Pressure Unit | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Flow Unit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Pressure Sensor Minimum Value [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Pressure Sensor Maximum Value [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Pressure Channel 2
|  |  | Pressure | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Pressure Unit | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Flow Unit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Pressure Sensor Minimum Value [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Pressure Sensor Maximum Value [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Output Channel 1
|  |  | Output channel 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Range channel 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Voltage channel 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Current channel 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Output Channel 2
|  |  | Output channel 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Range channel 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Current channel 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Voltage channel 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
About
Device ID
|  |  | Serial number | (SerialNumberString)
|  |  | Name | Device name, visible in App list (ControllerName)
|  |  | Description | Device description (ControllerDescription)
|  |  | Location | Device location (ControllerLocation)
|  |  | Project | Device project (ControllerProject)
Configuration
Display and menus
Display
|  |  | Start screen | What to display during device startup (DisplayStartupMode)
|  |  | Brightness full [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Display layout | Used to set the display layout. (PS_display_mode)
|  |  | Adaptive value toggle time | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Value toggle time [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Unit toggle time [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Channel toggle time [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Divider toggle time [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Scroll delay [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Sensor 1: Name | String to show on row 1 in the display (PS_1_text_row)
|  |  | Sensor 1: Unit | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Sensor 1: Additional Unit | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Sensor 1: Display Resolution [% Full Scale] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Sensor 2: Name | String to show on row 2 in the display (PS_2_text_row)
|  |  | Sensor 2: Unit | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Sensor 2: Additional Unit | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Sensor 2: Display Resolution [% Full Scale] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Custom Texts
|  |  | Scroll mode | Scroll mode (PS_display_text_scroll_mode)
|  |  | Font | What font to use for the display text (PS_display_text_font)
|  |  | Use custom text instead of Ch x tag | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Time to show custom text [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Custom text channel 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Custom text channel 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | External value 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | External value 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | External value 3 (Non volatile) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | External value 4 (Non volatile) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Pressure Channel 1
Common Settings
|  |  | Pressure sensor | Mode for input (IoAnaIn_4_mode)
|  |  | Filter time [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Output Resolution [% Full Scale] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Start Zero Calibration | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Pressure
|  |  | Pressure Unit | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Flow
|  |  | Flow Unit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow Formula | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Flow Air Density | Air density used on some flow calculations (PS_1_flow_air_density)
Pressure Channel 2
Common Settings
|  |  | Pressure sensor | Mode for input (IoAnaIn_5_mode)
|  |  | Filter time [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Output Resolution [% Full Scale] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Start Zero Calibration | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Pressure
|  |  | Pressure Unit | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Flow
|  |  | Flow Unit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow Formula | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Flow Air Density | Air density used on some flow calculations (PS_2_flow_air_density)
Output Channel 1
Mode
|  |  | Mode | Mode for output (IoAnaOut_1_mode)
|  |  | Range | Unit converter (IoAnaOut_1_unit)
Pressure Mapping
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Pressure at 0% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Pressure at 100% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Pressure at 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Pressure at 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Flow at 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Flow at 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Output Channel 2
Mode
|  |  | Mode | Mode for output (IoAnaOut_2_mode)
|  |  | Range | Unit converter (IoAnaOut_2_unit)
Pressure Mapping
|  |  | Pressure Range | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Pressure at 0% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Pressure at 100% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Pressure at 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Pressure at 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Flow at 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Flow at 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Manual/Auto
Hardware control
Output Channel 1
|  |  | Voltage channel 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Current channel 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Set value [0=0%, 100=100%] [%] | Override value (IoAnaOut_1_override)
Output Channel 2
|  |  | Current channel 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Voltage channel 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Set value [0=0%, 100=100%] [%] | Override value (IoAnaOut_2_override)
Pressure Channel 1
|  |  | Pressure | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Set value [Pa] | Override value (IoAnaIn_4_override)
Pressure Channel 2
|  |  | Pressure | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Set value [Pa] | Override value (IoAnaIn_5_override)
Device
Device ID
Device ID
|  |  | Name | Device name, visible in App list (ControllerName)
|  |  | Description | Device description (ControllerDescription)
|  |  | Location | Device location (ControllerLocation)
|  |  | Project | Device project (ControllerProject)
Communication
Bluetooth
|  |  | Bluetooth function | Function for BLE button (BleButtonMode)
|  |  | Turn off after [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE transmission power | BLE TX power level (ble_power)
Reset
Reset
|  |  | Restart controller | Write to this register will trigger resets with different reset reasons (product_reset)
Non volatile storage
Non volatile storage
|  |  | Disable non volatile storage | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## da
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Oversigt
System
|  |  | Enhed | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
Tryk kanal 1
|  |  | Tryk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Tryk enhed | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Flow enhed | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow K-faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Trykføler min. værdi [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Tryk føler maks. værdi [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Tryk kanal 2
|  |  | Tryk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Tryk enhed | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Flow enhed | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow K-faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Trykføler min. værdi [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Tryk føler maks. værdi [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Udgang kanal 1
|  |  | Udgang kanal 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Område kanal 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Spænding kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Aktuel kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Udgang kanal 2
|  |  | Udgang kanal 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Område kanal 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Aktuel kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spænding kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
Om
Enhed ID
|  |  | Serie nummer | (SerialNumberString)
|  |  | Navn | Device name, visible in App list (ControllerName)
|  |  | Beskrivelse | Device description (ControllerDescription)
|  |  | Lokation | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Konfiguration
Display og menuer
Display
|  |  | Start skærm | What to display during device startup (DisplayStartupMode)
|  |  | Lysstyrke fuld [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Display layout | Used to set the display layout. (PS_display_mode)
|  |  | Adaptiv værdi skifte tid | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Værdi skifte tid [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Enhed skifte tid [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Kanal skifte tid [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Opdeler skifte tid [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Rul forsinkelse [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Føler 1: Navn | String to show on row 1 in the display (PS_1_text_row)
|  |  | Føler 1: Enhed | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Føler 1: Yderligere enhed | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Føler 1: Displayopløsning [% fuld skala] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Føler 2: Navn | String to show on row 2 in the display (PS_2_text_row)
|  |  | Føler 2: Enhed | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Føler 2: Yderligere enhed | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Føler 2: Displayopløsning [% fuld skala] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Brugerdefinerede tekster
|  |  | Rul-tilstand | Scroll mode (PS_display_text_scroll_mode)
|  |  | Skrifttype | What font to use for the display text (PS_display_text_font)
|  |  | Brug brugerdefineret tekst i stedet for Ch x tag | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Tid til at vise brugerdefineret tekst [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Brugerdefineret tekstkanal 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Brugerdefineret tekstkanal 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | Ekstern værdi 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | Ekstern værdi 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | Ekstern værdi 3 (ikke-flygtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | Ekstern værdi 4 (ikke-flygtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Tryk kanal 1
Fælles indstillinger
|  |  | Tryksensor | Mode for input (IoAnaIn_4_mode)
|  |  | Filtreringstid [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Udgangsopløsning [% fuld skala] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Start nul kalibrering | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Tryk
|  |  | Tryk enhed | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Flow
|  |  | Flow enhed | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow formel | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Flow K-faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Flow luft densitet | Air density used on some flow calculations (PS_1_flow_air_density)
Tryk kanal 2
Fælles indstillinger
|  |  | Tryksensor | Mode for input (IoAnaIn_5_mode)
|  |  | Filtreringstid [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Udgangsopløsning [% fuld skala] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Start nul kalibrering | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Tryk
|  |  | Tryk enhed | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Flow
|  |  | Flow enhed | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow formel | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Flow K-faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Flow luft densitet | Air density used on some flow calculations (PS_2_flow_air_density)
Udgang kanal 1
Tilstand
|  |  | Tilstand | Mode for output (IoAnaOut_1_mode)
|  |  | Område | Unit converter (IoAnaOut_1_unit)
Tryk kortlægning
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryk ved 0 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Tryk ved 100 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Tryk ved 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Tryk ved 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Flow ved 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Flow ved 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Udgang kanal 2
Tilstand
|  |  | Tilstand | Mode for output (IoAnaOut_2_mode)
|  |  | Område | Unit converter (IoAnaOut_2_unit)
Tryk kortlægning
|  |  | Tryk område | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryk ved 0 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Tryk ved 100 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Tryk ved 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Tryk ved 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Flow ved 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Flow ved 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Manuel/Auto
Hardwarekontrol
Udgang kanal 1
|  |  | Spænding kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Aktuel kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_1_override)
Udgang kanal 2
|  |  | Aktuel kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spænding kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_2_override)
Tryk kanal 1
|  |  | Tryk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Indstillet værdi [Pa] | Override value (IoAnaIn_4_override)
Tryk kanal 2
|  |  | Tryk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Indstillet værdi [Pa] | Override value (IoAnaIn_5_override)
Enhed
Enhed ID
Enhed ID
|  |  | Navn | Device name, visible in App list (ControllerName)
|  |  | Beskrivelse | Device description (ControllerDescription)
|  |  | Lokation | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Kommunikation
Bluetooth
|  |  | Bluetooth funktion | Function for BLE button (BleButtonMode)
|  |  | Sluk efter [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE transmissionseffekt | BLE TX power level (ble_power)
Nulstil
Nulstil
|  |  | Genstart kontroller | Write to this register will trigger resets with different reset reasons (product_reset)
Ikke-flygtig lagring
Ikke-flygtig lagring
|  |  | Deaktiver ikke-flygtig lagring | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## de
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Übersicht
System
|  |  | Gerät | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
Druckkanal 1
|  |  | Druck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Druck Einheit | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Volumenstrom | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Volumenstrom Einheit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Volumenstrom K-Faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Druckfühler Minimalwert [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Druckfühler Maximalwert [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Druckkanal 2
|  |  | Druck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Druck Einheit | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Volumenstrom | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Volumenstrom Einheit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Volumenstrom K-Faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Druckfühler Minimalwert [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Druckfühler Maximalwert [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Ausgang Kanal 1
|  |  | Ausgang Kanal 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Bereich Kanal 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Spannung Kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Strom Kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Ausgang Kanal 2
|  |  | Ausgang Kanal 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Bereich Kanal 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Strom Kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spannung Kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
Info
Geräte-ID
|  |  | Seriennummer | (SerialNumberString)
|  |  | Name | Device name, visible in App list (ControllerName)
|  |  | Beschreibung | Device description (ControllerDescription)
|  |  | Standort | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Konfiguration
Display und Menüs
Display
|  |  | Startbildschirm | What to display during device startup (DisplayStartupMode)
|  |  | Volle Helligkeit [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Display-Layout | Used to set the display layout. (PS_display_mode)
|  |  | Anpassbare Umschaltzeit | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Umschaltzeit Wert [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Umschaltzeit Einheit [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Umschaltzeit Kanal [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Umschaltzeit Teiler [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Scrollverzögerung [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Fühler 1: Name | String to show on row 1 in the display (PS_1_text_row)
|  |  | Fühler 1: Einheit | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Fühler 1: Zusätzliche Einheit | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Fühler 1: Displayauflösung [% vom Messbereichsendwert] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Fühler 2: Name | String to show on row 2 in the display (PS_2_text_row)
|  |  | Fühler 2: Einheit | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Fühler 2: Zusätzliche Einheit | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Fühler 2: Displayauflösung [% vom Messbereichsendwert] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Benutzerdefinierte Texte
|  |  | Scrollmodus | Scroll mode (PS_display_text_scroll_mode)
|  |  | Schriftart | What font to use for the display text (PS_display_text_font)
|  |  | Benutzerdefinierter Text statt Chx-Tag | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Anzeigedauer benutzerdefinierter Text [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Benutzerdefinierter Text Kanal 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Benutzerdefinierter Text Kanal 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | Externer Wert 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | Externer Wert 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | Externer Wert 3 (nichtflüchtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | Externer Wert 4 (nichtflüchtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Druckkanal 1
Allgemeine Einstellungen
|  |  | Druckfühler | Mode for input (IoAnaIn_4_mode)
|  |  | Filterzeit [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Ausgabeauflösung [% vom Messbereichsendwert] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Nullpunktkalibrierung starten | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Druck
|  |  | Druck Einheit | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Volumenstrom
|  |  | Volumenstrom Einheit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Volumenstrom Formel | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Volumenstrom K-Faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Volumenstrom Luftdichte | Air density used on some flow calculations (PS_1_flow_air_density)
Druckkanal 2
Allgemeine Einstellungen
|  |  | Druckfühler | Mode for input (IoAnaIn_5_mode)
|  |  | Filterzeit [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Ausgabeauflösung [% vom Messbereichsendwert] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Nullpunktkalibrierung starten | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Druck
|  |  | Druck Einheit | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Volumenstrom
|  |  | Volumenstrom Einheit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Volumenstrom Formel | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Volumenstrom K-Faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Volumenstrom Luftdichte | Air density used on some flow calculations (PS_2_flow_air_density)
Ausgang Kanal 1
Betriebsmodus
|  |  | Betriebsmodus | Mode for output (IoAnaOut_1_mode)
|  |  | Bereich | Unit converter (IoAnaOut_1_unit)
Druckmessung
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druck bei 0 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Druck bei 100 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Druck bei 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Druck bei 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Volumenstrom bei 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Volumenstrom bei 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Ausgang Kanal 2
Betriebsmodus
|  |  | Betriebsmodus | Mode for output (IoAnaOut_2_mode)
|  |  | Bereich | Unit converter (IoAnaOut_2_unit)
Druckmessung
|  |  | Druckbereich | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druck bei 0 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Druck bei 100 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Druck bei 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Druck bei 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Volumenstrom bei 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Volumenstrom bei 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Hand/Auto
Hardwaresteuerung
Ausgang Kanal 1
|  |  | Spannung Kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Strom Kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_1_override)
Ausgang Kanal 2
|  |  | Strom Kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spannung Kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_2_override)
Druckkanal 1
|  |  | Druck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Einstellwert [Pa] | Override value (IoAnaIn_4_override)
Druckkanal 2
|  |  | Druck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Einstellwert [Pa] | Override value (IoAnaIn_5_override)
Gerät
Geräte-ID
Geräte-ID
|  |  | Name | Device name, visible in App list (ControllerName)
|  |  | Beschreibung | Device description (ControllerDescription)
|  |  | Standort | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Kommunikation
Bluetooth
|  |  | Bluetooth-Funktion | Function for BLE button (BleButtonMode)
|  |  | Ausschalten nach [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE Sendeleistung | BLE TX power level (ble_power)
Zurücksetzen
Zurücksetzen
|  |  | Regler Neustart | Write to this register will trigger resets with different reset reasons (product_reset)
Nichtflüchtiger Speicher
Nichtflüchtiger Speicher
|  |  | Nichtflüchtigen Speicher deaktivieren | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## fr
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Tableau de bord
Vue d’ensemble
Système
|  |  | Appareil | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
Pression Canal 1
|  |  | Pression | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Unité de pression | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Débit | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Unité de débit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Facteur K de débit | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Valeur minimale de la sonde de pression [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Valeur maximale de la sonde de pression [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Pression Canal 2
|  |  | Pression | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Unité de pression | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Débit | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Unité de débit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Facteur K de débit | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Valeur minimale de la sonde de pression [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Valeur maximale de la sonde de pression [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Sortie Canal 1
|  |  | Sortie Canal 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Plage Canal 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Tension Canal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Courant Canal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Sortie Canal 2
|  |  | Sortie Canal 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Plage Canal 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Courant Canal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Tension Canal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
À propos de…
ID d'appareil
|  |  | Nº de série | (SerialNumberString)
|  |  | Nom | Device name, visible in App list (ControllerName)
|  |  | Description | Device description (ControllerDescription)
|  |  | Emplacement | Device location (ControllerLocation)
|  |  | Projet | Device project (ControllerProject)
Configuration
Affichage et menus
Affichage
|  |  | Écran d'accueil | What to display during device startup (DisplayStartupMode)
|  |  | Luminosité totale [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Disposition de l'affichage | Used to set the display layout. (PS_display_mode)
|  |  | Temps de basculement de la valeur adaptative | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Durée d'affichage de valeur [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Durée d'affichage de l'unité [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Durée d'affichage du canal [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Durée d'affichage du diviseur [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Délai de défilement [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Sonde 1 : Nom | String to show on row 1 in the display (PS_1_text_row)
|  |  | Sonde 1 : Unité | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Sonde 1 : Unité supplémentaire | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Sonde 1 : Résolution de l’écran [% pleine échelle] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Sonde 2 : Nom | String to show on row 2 in the display (PS_2_text_row)
|  |  | Sonde 2 : Unité | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Sonde 2 : Unité supplémentaire | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Sonde 2 : Résolution de l’écran [% pleine échelle] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Textes personnalisés
|  |  | Mode défilement | Scroll mode (PS_display_text_scroll_mode)
|  |  | Police | What font to use for the display text (PS_display_text_font)
|  |  | Utiliser le texte personnalisé au lieu de la balise Ch x | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Temps d’affichage du texte personnalisé [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Texte personnalisé Canal 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Texte personnalisé Canal 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | Valeur externe 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | Valeur externe 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | Valeur externe 3 (non volatile) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | Valeur externe 4 (non volatile) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Pression Canal 1
Réglages communs
|  |  | Sonde de pression | Mode for input (IoAnaIn_4_mode)
|  |  | Temps de filtrage [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Résolution de sortie [% pleine échelle] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Lancer l'étalonnage à zéro | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Pression
|  |  | Unité de pression | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Débit
|  |  | Unité de débit | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Formule de débit | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Facteur K de débit | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Densité de l'air | Air density used on some flow calculations (PS_1_flow_air_density)
Pression Canal 2
Réglages communs
|  |  | Sonde de pression | Mode for input (IoAnaIn_5_mode)
|  |  | Temps de filtrage [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Résolution de sortie [% pleine échelle] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Lancer l'étalonnage à zéro | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Pression
|  |  | Unité de pression | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Débit
|  |  | Unité de débit | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Formule de débit | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Facteur K de débit | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Densité de l'air | Air density used on some flow calculations (PS_2_flow_air_density)
Sortie Canal 1
Mode
|  |  | Mode | Mode for output (IoAnaOut_1_mode)
|  |  | Plage | Unit converter (IoAnaOut_1_unit)
Mappage de la pression
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Pression à 0 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Pression à 100 % [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Pression à 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Pression à 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Débit à 0 % | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Débit à 100 % | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Sortie Canal 2
Mode
|  |  | Mode | Mode for output (IoAnaOut_2_mode)
|  |  | Plage | Unit converter (IoAnaOut_2_unit)
Mappage de la pression
|  |  | Plage de pression | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Pression à 0 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Pression à 100 % [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Pression à 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Pression à 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Débit à 0 % | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Débit à 100 % | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Manuel/Auto
Contrôle des sorties physiques
Sortie Canal 1
|  |  | Tension Canal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Courant Canal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_1_override)
Sortie Canal 2
|  |  | Courant Canal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Tension Canal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] [%] | Override value (IoAnaOut_2_override)
Pression Canal 1
|  |  | Pression | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Valeur réglée [Pa] | Override value (IoAnaIn_4_override)
Pression Canal 2
|  |  | Pression | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Valeur réglée [Pa] | Override value (IoAnaIn_5_override)
Appareil
ID d'appareil
ID d'appareil
|  |  | Nom | Device name, visible in App list (ControllerName)
|  |  | Description | Device description (ControllerDescription)
|  |  | Emplacement | Device location (ControllerLocation)
|  |  | Projet | Device project (ControllerProject)
Communication
Bluetooth
|  |  | Fonction Bluetooth | Function for BLE button (BleButtonMode)
|  |  | Arrêter après [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | Puissance d’émission BLE | BLE TX power level (ble_power)
Reset
Reset
|  |  | Redémarrer régulateur | Write to this register will trigger resets with different reset reasons (product_reset)
Stockage non volatil
Stockage non volatil
|  |  | Désactiver le stockage non volatil | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## nl
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overzicht
Systeem
|  |  | Apparaat | Model number (Model)
|  |  | Versie | The application version as a string (VersionNumberString)
Druk Kanaal 1
|  |  | Druk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Druk eenheid | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Flow eenheid | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Druksensor Minimum Waarde [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Druksensor Maximum Waarde [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Druk Kanaal 2
|  |  | Druk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Druk eenheid | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Flow | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Flow eenheid | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Druksensor Minimum Waarde [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Druksensor Maximum Waarde [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Uitgang Kanaal 1
|  |  | Uitgang kanaal 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Bereik kanaal 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Spanning kanaal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Stroom kanaal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Uitgang Kanaal 2
|  |  | Uitgangs kanaal 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Bereik kanaal 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Stroom kanaal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spanning kanaal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
Info
Apparaat-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Naam | Device name, visible in App list (ControllerName)
|  |  | Omschrijving | Device description (ControllerDescription)
|  |  | Locatie | Device location (ControllerLocation)
|  |  | Project | Device project (ControllerProject)
Configuratie
Display en menu's
Display
|  |  | Start scherm | What to display during device startup (DisplayStartupMode)
|  |  | Helderheid hoog [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Display indeling | Used to set the display layout. (PS_display_mode)
|  |  | Aanpasbare waarde wisselltijd | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Waarde wisseltijd [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Eenheid wisseltijd [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Kanaal wisseltijd [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Verdeler wisseltijd [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Scroll vertraging [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Sensor 1: Naam | String to show on row 1 in the display (PS_1_text_row)
|  |  | Sensor 1: Unit | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Sensor 1: Extra Unit | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Sensor 1: Weergave resolutie [% volledige schaal] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Sensor 2: Naam | String to show on row 2 in the display (PS_2_text_row)
|  |  | Sensor 2: Unit | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Sensor 2: Extra Unit | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Sensor 2: Weergave resolutie [% volledige schaal] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Aangepaste teksten
|  |  | Scroll modus | Scroll mode (PS_display_text_scroll_mode)
|  |  | Lettertype | What font to use for the display text (PS_display_text_font)
|  |  | Gebruik aangepaste tekst in plaats van Ch x tag | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Tijd om aangepaste tekst weer te geven [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Aangepaste tekst kanaal 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Aangepaste tekst kanaal 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | Externe waarde 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | Externe waarde 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | Externe waarde 3 (niet-vluchtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | Externe waarde 4 (niet-vluchtig) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Druk Kanaal 1
Gemeenschappelijke Instellingen
|  |  | Druksensor | Mode for input (IoAnaIn_4_mode)
|  |  | Filtertijd [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Uitgang resolutie [% volledige schaal] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Nulkalibratie starten | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Druk
|  |  | Druk eenheid | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Flow
|  |  | Flow eenheid | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flow Formule | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Flow Luchtdichtheid | Air density used on some flow calculations (PS_1_flow_air_density)
Druk Kanaal 2
Gemeenschappelijke Instellingen
|  |  | Druksensor | Mode for input (IoAnaIn_5_mode)
|  |  | Filtertijd [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Uitgang resolutie [% volledige schaal] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Nulkalibratie starten | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Druk
|  |  | Druk eenheid | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Flow
|  |  | Flow eenheid | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flow Formule | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Flow K-factor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Flow Luchtdichtheid | Air density used on some flow calculations (PS_2_flow_air_density)
Uitgang Kanaal 1
Modus
|  |  | Modus | Mode for output (IoAnaOut_1_mode)
|  |  | Bereik | Unit converter (IoAnaOut_1_unit)
Druk meting en visualisatie
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Druk bij 0% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Druk bij 100% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Druk bij 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Druk bij 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Flow bij 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Flow bij 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Uitgang Kanaal 2
Modus
|  |  | Modus | Mode for output (IoAnaOut_2_mode)
|  |  | Bereik | Unit converter (IoAnaOut_2_unit)
Druk meting en visualisatie
|  |  | Druk bereik | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Druk bij 0% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Druk bij 100% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Druk bij 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Druk bij 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Flow bij 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Flow bij 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Handmatig/Auto
Hardware regeling
Uitgang Kanaal 1
|  |  | Spanning kanaal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Stroom kanaal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] [%] | Override value (IoAnaOut_1_override)
Uitgang Kanaal 2
|  |  | Stroom kanaal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spanning kanaal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] [%] | Override value (IoAnaOut_2_override)
Druk Kanaal 1
|  |  | Druk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Gewenst [Pa] | Override value (IoAnaIn_4_override)
Druk Kanaal 2
|  |  | Druk | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Gewenst [Pa] | Override value (IoAnaIn_5_override)
Apparaat
Apparaat-ID
Apparaat-ID
|  |  | Naam | Device name, visible in App list (ControllerName)
|  |  | Omschrijving | Device description (ControllerDescription)
|  |  | Locatie | Device location (ControllerLocation)
|  |  | Project | Device project (ControllerProject)
Communicatie
Bluetooth
|  |  | Bluetooth-functie | Function for BLE button (BleButtonMode)
|  |  | Uitschakeling na [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE zendvermogen | BLE TX power level (ble_power)
Reset
Reset
|  |  | Herstart regelaar | Write to this register will trigger resets with different reset reasons (product_reset)
Niet-vluchtig geheugen
Niet-vluchtig geheugen
|  |  | Niet-vluchtig geheugen uitschakelen | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## sv
PDTN-1.1-1-00 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Översikt
System
|  |  | Enhet | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
Tryck, kanal 1
|  |  | Tryck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Tryckenhet | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
|  |  | Flöde | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_1_flow)
|  |  | Flödesenhet | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flöde K-faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Minimalt värde för tryckgivare [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MinPressure)
|  |  | Maximalt värde för tryckgivare [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_1_MaxPressure)
Tryck, kanal 2
|  |  | Tryck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Tryckenhet | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
|  |  | Flöde | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA (PS_2_flow)
|  |  | Flödesenhet | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flöde K-faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Minimalt värde för tryckgivare [Pa] | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MinPressure)
|  |  | Maximalt värde för tryckgivare [Pa] | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor (PS_2_MaxPressure)
Utgång kanal 1
|  |  | Utgångskanal 1 [%] | Value in % set for output (IoAnaOut_1_value)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Intervall kanal 1 | Unit converter (IoAnaOut_1_unit)
|  |  | Spänning kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Aktuell kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
Set to 1 to enable override (IoAnaOut_1_override_en)
Utgång kanal 2
|  |  | Utgångskanal 2 [%] | Value in % set for output (IoAnaOut_2_value)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Intervall kanal 2 | Unit converter (IoAnaOut_2_unit)
|  |  | Aktuell kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spänning kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
Set to 1 to enable override (IoAnaOut_2_override_en)
Om
Enhets-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Namn | Device name, visible in App list (ControllerName)
|  |  | Beskrivning | Device description (ControllerDescription)
|  |  | Plats | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Konfigurering
Display och menyer
Display
|  |  | Startskärm | What to display during device startup (DisplayStartupMode)
|  |  | Full ljusstyrka [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Displaylayout | Used to set the display layout. (PS_display_mode)
|  |  | Växlingstid för adaptivt värde | Adaptive Time for Display: Activate the adaptive time display for single row displays (AdaptTimeDisp_ACTIVATE)
|  |  | Värde växlingstid [ms] | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. (PS_display_value_time_ms)
|  |  | Enhet växlingstid [ms] | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. (PS_display_unit_time_ms)
|  |  | Kanal växlingstid [ms] | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode (PS_display_channel_time_ms)
|  |  | Avdelare växlingstid [ms] | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. (PS_display_split_time_ms)
|  |  | Bläddring, fördröjning [ms] | Time in ms between scrolling one pixel (PS_display_text_scroll_speed)
|  |  | Givare 1: Namn | String to show on row 1 in the display (PS_1_text_row)
|  |  | Givare 1: Enhet | Used to set the displayed value in the display (PS_1_display_unit)
|  |  | Givare 1: Extra enhet | Used to set an additional value to be displayed for this channel. (PS_1_display_extra_unit)
|  |  | Givare 1: Displayens upplösning [% full skala] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_1_display_resolution)
|  |  | Givare 2: Namn | String to show on row 2 in the display (PS_2_text_row)
|  |  | Givare 2: Enhet | Used to set the displayed value in the display (PS_2_display_unit)
|  |  | Givare 2: Extra enhet | Used to set an additional value to be displayed for this channel. (PS_2_display_extra_unit)
|  |  | Givare 2: Displayens upplösning [% full skala] [%] | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. (PS_2_display_resolution)
Anpassade texter
|  |  | Bläddringsläge | Scroll mode (PS_display_text_scroll_mode)
|  |  | Teckensnitt | What font to use for the display text (PS_display_text_font)
|  |  | Använd anpassad text istället för Ch x tag | In single row, replace the CHx tag with this text (PS_display_text_replace_chn_tag)
|  |  | Tid att visa anpassad text [ms] | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. (PS_display_text_time_ms)
|  |  | Anpassad text kanal 1 | String to show on row 1 in the display (PS_1_text_row)
|  |  | Anpassad text kanal 2 | String to show on row 2 in the display (PS_2_text_row)
|  |  | Externt värde 1 | Can be used as @15# or @16# in custom text (ext_value_1)
|  |  | Externt värde 2 | Can be used as @15# or @16# in custom text (ext_value_2)
|  |  | Externt värde 3 (icke-flyktigt) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_3)
|  |  | Externt värde 4 (icke-flyktigt) | Can be used as @17# or @18# in custom text (ext_value_nonvolatile_4)
Tryck, kanal 1
Standardinställningar
|  |  | Tryckgivare | Mode for input (IoAnaIn_4_mode)
|  |  | Filtertid [s] | Filter time (0 to 17200 seconds) (IoAnaIn_4_filter)
|  |  | Utgångsupplösning [% full skala] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_1_resolution)
|  |  | Starta nollkalibrering | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_1_set_zero)
Tryck
|  |  | Tryckenhet | Used to convert the pressure sensor output value to the preferred unit (PS_1_unit)
Flöde
|  |  | Flödesenhet | Used to convert the pressure sensor output value to the preferred unit. (PS_1_flow_unit)
|  |  | Flödesformel | The formula used to calculate the flow from the measured pressure (PS_1_flow_formula)
|  |  | Flöde K-faktor | The K factor used in the flow calculation (PS_1_flow_k_factor)
|  |  | Luftflödesdensitet | Air density used on some flow calculations (PS_1_flow_air_density)
Tryck, kanal 2
Standardinställningar
|  |  | Tryckgivare | Mode for input (IoAnaIn_5_mode)
|  |  | Filtertid [s] | Filter time (0 to 17200 seconds) (IoAnaIn_5_filter)
|  |  | Utgångsupplösning [% full skala] [%] | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy (PS_2_resolution)
|  |  | Starta nollkalibrering | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. (PS_2_set_zero)
Tryck
|  |  | Tryckenhet | Used to convert the pressure sensor output value to the preferred unit (PS_2_unit)
Flöde
|  |  | Flödesenhet | Used to convert the pressure sensor output value to the preferred unit. (PS_2_flow_unit)
|  |  | Flödesformel | The formula used to calculate the flow from the measured pressure (PS_2_flow_formula)
|  |  | Flöde K-faktor | The K factor used in the flow calculation (PS_2_flow_k_factor)
|  |  | Luftflödesdensitet | Air density used on some flow calculations (PS_2_flow_air_density)
Utgång kanal 1
Driftläge
|  |  | Driftläge | Mode for output (IoAnaOut_1_mode)
|  |  | Intervall | Unit converter (IoAnaOut_1_unit)
Mappning Tryck
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_1_pressure as source. 12: Use custom mapping with PS_1_flow as source. 20: Disable mapping (PS_1_range)
|  |  | Tryck vid 0% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Tryck vid 100% [Pa] | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Tryck vid 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Tryck vid 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
|  |  | Flöde vid 0% | Used for custom Mapping och analog output range (PS_1_MapMinPressure)
|  |  | Flöde vid 100% | Used for custom Mapping och analog output range (PS_1_MapMaxPressure)
Utgång kanal 2
Driftläge
|  |  | Driftläge | Mode for output (IoAnaOut_2_mode)
|  |  | Intervall | Unit converter (IoAnaOut_2_unit)
Mappning Tryck
|  |  | Tryckintervall | Range Selected by switch. 0-9: See manual for corresponding range 10: Use custom mapping. 11: Use custom mapping with PS_2_pressure as source. 12: Use custom mapping with PS_2_flow as source. 20: Disable mapping (PS_2_range)
|  |  | Tryck vid 0% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Tryck vid 100% [Pa] | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Tryck vid 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Tryck vid 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
|  |  | Flöde vid 0% | Used for custom Mapping och analog output range (PS_2_MapMinPressure)
|  |  | Flöde vid 100% | Used for custom Mapping och analog output range (PS_2_MapMaxPressure)
Manuell/Auto
Hårdvarustyrning
Utgång kanal 1
|  |  | Spänning kanal 1 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Aktuell kanal 1 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Inställt värde [0=0%, 100=100%] [%] | Override value (IoAnaOut_1_override)
Utgång kanal 2
|  |  | Aktuell kanal 2 [mA] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Spänning kanal 2 [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Inställt värde [0=0%, 100=100%] [%] | Override value (IoAnaOut_2_override)
Tryck, kanal 1
|  |  | Tryck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_1_pressure)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_4_override_en)
|  |  | Inställt värde [Pa] | Override value (IoAnaIn_4_override)
Tryck, kanal 2
|  |  | Tryck | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. (PS_2_pressure)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_5_override_en)
|  |  | Inställt värde [Pa] | Override value (IoAnaIn_5_override)
Enhet
Enhets-ID
Enhets-ID
|  |  | Namn | Device name, visible in App list (ControllerName)
|  |  | Beskrivning | Device description (ControllerDescription)
|  |  | Plats | Device location (ControllerLocation)
|  |  | Projekt | Device project (ControllerProject)
Kommunikation
Bluetooth
|  |  | Bluetooth-funktion | Function for BLE button (BleButtonMode)
|  |  | Stäng av efter [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE-sändningseffekt | BLE TX power level (ble_power)
Återställ
Återställ
|  |  | Starta om regulator | Write to this register will trigger resets with different reset reasons (product_reset)
Icke-flyktig lagring
Icke-flyktig lagring
|  |  | Inaktivera icke-flyktig lagring | Set to 1 to disable storage in non volatile memory (disable_nv_storage)