## Info
Name | RCX
Version | 2.0-1-02
Description | MODEL 2.0-1-02

## en
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overview
System
|  |  | Controller | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
Room
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
|  |  | Supply air temperature (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Room setpoint (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC fan speed (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 level (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Room humidity (%) | Relative humidity (RC_Humidity)
|  |  | VOC index | VOC index (RC_VOC)
|  |  | Presence detection | Presence indication (RC_Presence)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Extra zone
|  |  | Extra zone temperature (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zone setpoint (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Actual values
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Actual values
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
|  |  | Room setpoint (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Heating demand (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Cooling demand (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Heating output (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Heating 2 output (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Cooling output (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Cooling 2 output (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV output (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 output (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperature | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over state | Change-over status (RC_ChangeOverState)
|  |  | Change-over output (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV temperature | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV state | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV output (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-way valve output (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 level (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 setpoint (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
|  |  | Source 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Source 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Source 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Source 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timer state | Current timer state (rt_exttime_state)
|  |  | Active timer value | Time remaining (rt_exttime_timeleft)
Inputs/Outputs
Universal inputs
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universal outputs
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analog outputs
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Internal sensors
|  |  | Room temperature (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 sensor (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RH sensor (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
Alarms
Alarms
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
|  |  | Sensor error | Sensor error alarm (RC_AlarmSensorError)
|  |  | High room temperature | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Low room temperature | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | High CO2 level | High CO2 alarm (RC_AlarmCO2High)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Output in manual mode | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Temperature sensor error code | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Humidity sensor error code | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | VOC sensor error code | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | CO2 sensor error code | Detailed fault description (IoAnaIn_8_errorFlags)
About
Controller ID
|  |  | Serial number | (SerialNumberString)
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Configuration
Control functions
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Heat
|  |  | Max limit (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min limit (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Fan off delay for electric heater | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Follow change-over state | Heat1 included in change-over function (RC_Heat1InChangeOver)
Heat 2
|  |  | Max limit (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min limit (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Fan off delay for electric heater | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Follow change-over state | Heat2 included in change-over function (RC_Heat2InChangeOver)
Cool
|  |  | Max limit (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min limit (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Follow change-over state | Cool1 included in change-over function (RC_Cool1InChangeOver)
Cool 2
|  |  | Max limit (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min limit (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Follow change-over state | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max limit (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min limit, off (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min limit, unoccupied (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min limit, standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min limit, occupied (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max limit when heating (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Follow change-over state | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Max limit (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min limit, off (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min limit, unoccupied (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min limit, standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min limit, occupied (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max limit when heating (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Follow change-over state | VAV2 included in change-over function (RC_VAV2InChangeOver)
VAV control source
|  |  | Cooling demand | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 level | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Humidity | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max limit (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min limit (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Mode | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperature (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Heating hysteresis (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Cooling hysteresis (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Valve delay time (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Max limit (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min limit, off (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min limit, unoccupied (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min limit, standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min limit, occupied (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Set to max at forced ventilation state | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Mode | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperature (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Heating hysteresis (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Cooling hysteresis (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Valve delay time (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-way valve
|  |  | Seq 1 fully open (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Seq 1 start opening (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Seq 2 fully open (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Seq 2 start opening (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Center point (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Center point hysteresis (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sequence order | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Follow change-over state | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Controller state
|  |  | Preset state | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Shutdown state | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Window open state | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Time in forced ventilation state (min) | Bypass time (minutes) (RC_BypassTime)
Forced ventilation
|  |  | Active when | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start limit (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Presence detection
|  |  | Presence state | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Active delay (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inactive delay (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 activation | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 level (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysteresis (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Use internal PIR for presence | Use internal PID sensor for presence detection (RC_PIDPresence)
Extra zone
Extra zone
|  |  | Extra zone function | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Disabled below state | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Disable if main zone mode differs from function | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min limit (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max limit (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Inputs/Outputs
Universal inputs
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universal outputs
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 period thermal valve (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 control signal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 period thermal valve (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 control signal | Unit converter (IoAnaOut_2_unit)
Analog outputs
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 control signal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 control signal | Unit converter (IoAnaOut_4_unit)
Fan control
Fan control source
|  |  | Room controller | Select fan control mode (RC_FanControlMode)
|  |  | CO2 level | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Humidity | Fan is controlled by humidity output (RC_FanControlHumidity)
EC Fan control
|  |  | Speed at no demand | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Off below demand (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysteresis for fan speed decrease (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start speed (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max speed in auto mode (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Forced ventilation speed | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Forced ventilation speed (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Speed 1 output (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Speed 2 output (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Speed 3 output (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Mould protection | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Fan kick start
|  |  | Kick-start time (s) | Fan kick start time (RC_FanKickStartTime)
Fan off delay
|  |  | Off delay time (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimum speed | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Fan boost
|  |  | Mode | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost time (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display and menus
Display
|  |  | Start screen | What to display during device startup (DisplayStartupMode)
|  |  | View mode | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Alternate temp/CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Setpoint mode | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Round CO2 value to nearest | Min step for CO2 value (RC_CO2Step)
|  |  | Brightness full (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dim timeout, 0 = Always full (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Brightness dimmed (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Off timeout, 0 = Never off (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Values to display
Timer
|  |  | Display mode | How to show the timer in the display (rt_exttime_mode)
|  |  | Animation | Show animation in timer view (rt_exttime_animate)
|  |  | Turn on LED when active | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Step size in minutes (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Number of steps | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Current timer value (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timer state | Current timer state (rt_exttime_state)
Custom Texts
|  |  | View mode | When to show the custom text (rt_text_visability)
|  |  | Display mode | Single or dual row text in display (rt_text_mode)
|  |  | Scroll mode | Scroll mode (rt_text_display_scroll_mode)
|  |  | Font | What font to use for the display text (rt_text_font)
|  |  | Scroll delay (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Custom text timer value (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Custom text row 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text row 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Custom text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text 2 | String to show on row 2 in the display (rt_text_row_2)
Led indication
|  |  | Brightness (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 led indication | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Yellow led CO2 level (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Red led CO2 level (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menu
|  |  | Setpoint adjust | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Mode menu page | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu page | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Fan menu page | Enable Fan menu page (App_EnableMenuFan)
|  |  | Forced ventilation menu page | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Forced ventilation extended run | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Humidity menu page | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu page | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu page | Enable VOC menu page (App_EnableMenuVOC)
Mode menu options
|  |  | Menu title text | Mode menu title (App_ModeMenuTitle)
|  |  | Mode Off enable | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Mode Unoccupied enable | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Mode Standby enable | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Mode Occupied enable | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Mode Forced ventilation enable | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Mode Off text | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Mode Unoccupied text | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Mode Standby text | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Mode Occupied text | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Mode Forced ventilation text | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Mode Auto text | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menu options
|  |  | Menu title text | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | State Heat enable | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | State Cool enable | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | State Auto enable | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | State Heat text | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | State Cool text | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | State Auto text | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Actuators
On/off outputs
|  |  | Heating hysteresis, room temperature (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Cooling hysteresis, room temperature (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysteresis, extra zone temperature (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Valve exercise
|  |  | Exercise valves | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Heat interval (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Heat 2 interval (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Cool interval (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Cool 2 interval (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-over interval (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-way valve interval (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Heat duration (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Heat 2 duration (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Cool duration (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Cool 2 duration (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over duration (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-way valve duration (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analog inputs
Temperature input
|  |  | Filter time (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperature input 0-10V
|  |  | Value at 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Value at 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 input
|  |  | Value at 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Value at 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filter time (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Humidity input
|  |  | Value at 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Value at 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filter time (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow input
|  |  | Value at 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Value at 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filter time (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC input
|  |  | Value at 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Value at 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filter time (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Setpoints
Room setpoints
|  |  | Heating, occupied (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Cooling, occupied (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Heating, standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Cooling, standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Heating, unoccupied (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Cooling, unoccupied (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frost protection (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Setpoint adjustment
|  |  | Max up adjustment (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max down adjustment (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zone
|  |  | Extra zone setpoint (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 setpoint (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Humidity
|  |  | Humidity setpoint (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC setpoint | Setpoint for VOC control (RC_VOCSetpoint)
Controller settings
Room
|  |  | P-band (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-time (s) | I-time for room PID controller (RC_RoomPIDItime)
Cascade control
|  |  | Control active | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Cascade factor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max heating temperature (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min heating temperature (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max cooling temperature (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min cooling temperature (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frost protection temperature (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zone
|  |  | P-band (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-time (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-time (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Humidity
|  |  | P-band (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-time (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-time (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm settings
Room temperature alarm
|  |  | High limit (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Low limit (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2 level alarm
|  |  | High limit (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Input adjustments
UI1
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_1_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_1_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_1_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_1_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_2_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_2_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_2_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_2_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_2_offset)
Room temperature
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_5_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_5_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_5_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_5_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_5_offset)
Room humidity
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_6_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_6_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_6_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_6_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_6_offset)
VOC sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_7_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_7_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_7_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_7_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_7_offset)
CO2 sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_8_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_8_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_8_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_8_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_8_offset)
Output adjustments
UO1
|  |  | Minimum value | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimum value | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimum value | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimum value | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Manual/Auto
Remote input values
Room temperature
|  |  | Remote setting | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
Supply air temperature
|  |  | Remote setting | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Supply air temperature (°C) | Supply air temperature (RC_SupplyAirTemp)
Extra zone temperature
|  |  | Remote setting | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zone temperature (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperature
|  |  | Remote setting | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperature (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV temperature
|  |  | Remote setting | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV temperature (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 level
|  |  | Remote setting | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Set value (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 level (ppm) | Room CO2 level (RC_CO2Level)
Room humidity
|  |  | Remote setting | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Set value (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Room humidity (%) | Relative humidity (RC_Humidity)
Air Flow
|  |  | Remote setting | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Set value | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Air Flow | Air flow (RC_AirFlow)
VOC index
|  |  | Remote setting | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Set value | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC index | VOC index (RC_VOC)
Presence detection
|  |  | Remote setting | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Set value | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Presence detection | Presence indication (RC_Presence)
Open window
|  |  | Remote setting | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Set value | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Open window | Open window indication (RC_DIOpenWindow)
Condensation
|  |  | Remote setting | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Set value | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensation | Condensation indication (RC_DICondensation)
External alarm (DI)
|  |  | Remote setting | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Set value | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Remote setting | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Set value | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Remote setting | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Set value | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manual/Auto
Controller state
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Remote state setting | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Shutdown | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Forced ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Fan control source
|  |  | Fan control source | Fan speed setting (RC_FanSelect)
Heating output
|  |  | Mode | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Heating output (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Mode | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Heating output | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Heating 2 output
|  |  | Mode | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Heating 2 output (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Mode | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Heating 2 output | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Cooling output
|  |  | Mode | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Cooling output (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Mode | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Cooling output | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Cooling 2 output
|  |  | Mode | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Cooling 2 output (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Mode | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Cooling 2 output | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV output
|  |  | Mode | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV output (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 output
|  |  | Mode | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 output (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over output
|  |  | Mode | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Set value (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over output (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV output
|  |  | Mode | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Set value (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV output (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-way valve output
|  |  | Mode | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Mode | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Set value (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-way valve output (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extra zone output
|  |  | Mode | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Set value (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extra zone output | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC Fan control
|  |  | Mode | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Set value (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC Fan control (%) | Current EC fan speed (RC_ECFanSpeed)
CO2 control output
|  |  | Mode | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Set value (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 control output (%) | CO2 control analog out (RC_CO2ControlAO)
Humidify control output
|  |  | Mode | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Set value (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Humidify control output (%) | Humidify analog out (RC_HumidifyOutputAO)
Dehumidify control output
|  |  | Mode | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Set value (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Dehumidify control output (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC control output
|  |  | Mode | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Set value (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC control output (%) | VOC control analog out (RC_VOCControlAO)
Extra zone active output
|  |  | Mode | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Forced ventilation output
|  |  | Mode | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Forced ventilation output | Forced ventilation output (RC_ForcedVentDO)
Hardware control
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Mode | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Set value | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Mode | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Set value | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Set value | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Set value | Override value (IoAnaIn_2_override)
CO2 sensor calibration
|  |  | Enable automatic self calibration | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatic self calibration baseline [ppm] (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Run CO2 sensor forced recalibration | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Reference CO2 level for forced recalibration [ppm] (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Last forced recalibration offset (-9999 = Error) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Reset CO2 sensor | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
|  |  | Mode | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Set value | Override value (IoDo_3_override)
PIR sensor
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Mode | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Set value | Override value (IoDiIn_4_override)
Device
Controller ID
Controller ID
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Communication
Port settings
|  |  | Port 1 function | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 parity | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP max master address | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet device object name | BACnet device object name (BACnetDeviceObjectName)
|  |  | Password | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth function | Function for BLE button (BleButtonMode)
|  |  | Turn off after (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Communication fail
|  |  | Fail action | Offline function (RC_OfflineFunction)
|  |  | Timeout (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback state | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Restart controller | Write to this register will trigger resets with different reset reasons (product_reset)

## da
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Oversigt
System
|  |  | Controller | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus adresse | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet enheds ID | BACnet device ID (BACnetDeviceID)
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
Rum
|  |  | Controller tilstand | Current state (RC_ControllerState)
|  |  | Tilstand | Current controller mode (RC_ControllerMode)
|  |  | Rumtemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Tilluft temperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Rum sætpunkt (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sætpunkts justering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC ventilator hastighed (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 niveau (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Rum fugtighed (%) | Relative humidity (RC_Humidity)
|  |  | VOC indeks | VOC index (RC_VOC)
|  |  | Tilstedeværelses detektering | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Ekstra zone
|  |  | Ekstra zone temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Ekstra zone sætpunkt (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Ekstra zone aktiv udgang | Extra Zone active (RC_ExtraZoneActive)
Aktuel værdi
Rum kontrol sekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Aktuel værdi
|  |  | Tilstand | Current controller mode (RC_ControllerMode)
|  |  | Rumtemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Rum sætpunkt (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sætpunkts justering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Varme behov (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Køle behov (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Varme udgang (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Varme 2 udgang (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Køling udgang (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Køling 2 udgang (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV udgang (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 udgang (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over tilstand | Change-over status (RC_ChangeOverState)
|  |  | Change-over udgang (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV tilstand | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV udgang (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-vejsventil udgang (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 niveau (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 sætpunkt (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Relæ udgang
|  |  | Relæ status | Value set for output (IoDo_3_value)
|  |  | Kilde 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Deaktiver grænse | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Aktivér grænse | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Kilde 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Deaktiver grænse | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Aktivér grænse | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Kilde 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Deaktiver grænse | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Aktivér grænse | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Kilde 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Deaktiver grænse | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Aktivér grænse | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timer tilstand | Current timer state (rt_exttime_state)
|  |  | Aktiv timer værdi | Time remaining (rt_exttime_timeleft)
Indgange/udgange
Universal indgange
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universal udgange
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoge udgange
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne følere
|  |  | Rumtemperatur (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 føler (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RH føler (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC føler | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR føler | Filtered value from sensor (IoDiIn_4_value)
Alarmer
Alarmer
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
|  |  | Føler fejl | Sensor error alarm (RC_AlarmSensorError)
|  |  | Høj rumtemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Lav rumtemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Højt CO2 niveau | High CO2 alarm (RC_AlarmCO2High)
|  |  | Ekstern alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Udgang i manuel tilstand | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Temperatur føler fejl kode | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Fugtighed føler fejl kode | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | VOC føler fejl kode | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | CO2 føler fejl kode | Detailed fault description (IoAnaIn_8_errorFlags)
Om
Kontroller ID
|  |  | Serie nummer | (SerialNumberString)
|  |  | Navn | (ControllerName)
|  |  | Beskrivelse | Controller description (ControllerDescription)
|  |  | Lokation | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Konfiguration
Kontrolfunktioner
Rum kontrol sekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Varme
|  |  | Maks. grænse (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min. grænse (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Ventilator fra- forsinkelse for elektrisk varmelegeme | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Følg change-over tilstand | Heat1 included in change-over function (RC_Heat1InChangeOver)
Varme 2
|  |  | Maks. grænse (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min. grænse (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Ventilator fra- forsinkelse for elektrisk varmelegeme | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Følg change-over tilstand | Heat2 included in change-over function (RC_Heat2InChangeOver)
Køle
|  |  | Maks. grænse (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min. grænse (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Følg change-over tilstand | Cool1 included in change-over function (RC_Cool1InChangeOver)
Køle 2
|  |  | Maks. grænse (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min. grænse (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Følg change-over tilstand | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Maks. grænse (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min. grænse, fra (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min. grænse, unoccupied (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min. grænse, standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min. grænse, occupied (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Maks. grænse ved varme (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Følg change-over tilstand | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Maks. grænse (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min. grænse, fra (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min. grænse, unoccupied (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min. grænse, standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min. grænse, occupied (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Maks. grænse ved varme (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Følg change-over tilstand | VAV2 included in change-over function (RC_VAV2InChangeOver)
VAV styre kilde
|  |  | Køle behov | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 niveau | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC indeks | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Fugtighed | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Maks. grænse (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min. grænse (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Tilstand | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Varme hysterese (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Køling hysterese (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Ventil forsinkelsestid (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Maks. grænse (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min. grænse, fra (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min. grænse, unoccupied (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min. grænse, standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min. grænse, occupied (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Tilstand | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Varme hysterese (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Køling hysterese (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Ventil forsinkelsestid (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-vejsventil
|  |  | Sekv. 1 helt åben (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Sekv. 1 start åbning (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Sekv. 2 helt åben (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Sekv. 2 start åbning (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Midterpunkt (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Midterpunkt hysterese (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sekvensrækkefølge | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Følg change-over tilstand | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Controller tilstand
|  |  | Forudindstillet tilstand | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Nedluknings tilstand | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Vindue åbent tilstand | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tid i tvungen ventilations tilstand (min) | Bypass time (minutes) (RC_BypassTime)
Tvungen ventilation
|  |  | Aktiv, når | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start grænse (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Tilstedeværelses detektering
|  |  | Tilstedeværelses tilstand | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Aktiv forsinkelse (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inaktiv forsinkelse (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 aktivering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 niveau (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysterese (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Brug intern PIR til tilstedeværelse | Use internal PID sensor for presence detection (RC_PIDPresence)
Ekstra zone
Ekstra zone
|  |  | Ekstra zone funktion | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Deaktiveret under tilstand | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Deaktiver, hvis hovedzonetilstand afviger fra funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min. grænse (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Maks. grænse (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Indgange/udgange
Universal indgange
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universal udgange
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 periode termisk ventil (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 styresignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 periode termisk ventil (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 styresignal | Unit converter (IoAnaOut_2_unit)
Analoge udgange
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 styresignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 styresignal | Unit converter (IoAnaOut_4_unit)
Ventilator kontrol
Ventilator styre kilde
|  |  | Rum kontroller | Select fan control mode (RC_FanControlMode)
|  |  | CO2 niveau | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Fugtighed | Fan is controlled by humidity output (RC_FanControlHumidity)
EC ventilator styring
|  |  | Hastighed uden behov | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Fra under behov (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese for reduktion af ventilator hastighed (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start hastighed (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Maks. hastighed i automatisk tilstand (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Tvungen ventilation hastighed | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Tvungen ventilation hastighed (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Hastighed 1 udgang (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Hastighed 2 udgang (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Hastighed 3 udgang (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Skimmel beskyttelse | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Ventilator kickstart
|  |  | Kickstart-tid (s) | Fan kick start time (RC_FanKickStartTime)
Ventilator fra- forsinkelse
|  |  | Fra forsinkelses tid (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Min. hastighed | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilator boost
|  |  | Tilstand | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost-tid (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-bånd | Fan boost P band (RC_FanBoostPBand)
Display og menuer
Display
|  |  | Start skærm | What to display during device startup (DisplayStartupMode)
|  |  | Visning tilstand | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Alternativ temp/CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Sætpunkt tilstand | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Afrund CO2 værdi til nærmeste | Min step for CO2 value (RC_CO2Step)
|  |  | Lysstyrke fuld (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dæmpnings timeout, 0 = Altid fuld (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Lysstyrke dæmpet (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Fra timeout, 0 = Aldrig Fra (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Værdier på display
Timer
|  |  | Display tilstand | How to show the timer in the display (rt_exttime_mode)
|  |  | Animation | Show animation in timer view (rt_exttime_animate)
|  |  | Tænd LED når aktiv | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Trin størrelse i minutter (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Antal trin | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Aktuel timer værdi (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timer tilstand | Current timer state (rt_exttime_state)
Brugerdefinerede tekster
|  |  | Visning tilstand | When to show the custom text (rt_text_visability)
|  |  | Display tilstand | Single or dual row text in display (rt_text_mode)
|  |  | Rul-tilstand | Scroll mode (rt_text_display_scroll_mode)
|  |  | Skrifttype | What font to use for the display text (rt_text_font)
|  |  | Rul forsinkelse (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Bruger defineret tekst timer værdi (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Brugerdefineret tekst række 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Brugerdefineret tekst række 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Brugerdefineret tekst 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Brugerdefineret tekst 2 | String to show on row 2 in the display (rt_text_row_2)
LED indikation
|  |  | Lysstyrke (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED indikation | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gul LED CO2 niveau (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rød LED CO2 niveau (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menu
|  |  | Sætpunkts justering | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Tilstand menu side | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu side | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator menu side | Enable Fan menu page (App_EnableMenuFan)
|  |  | Tvungen ventilation menu side | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Tvungen ventilation forlænget drift | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Fugtighed menu side | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu side | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu side | Enable VOC menu page (App_EnableMenuVOC)
Menuvalg muligheder
|  |  | Menu titel tekst | Mode menu title (App_ModeMenuTitle)
|  |  | Tilstand Fra aktiveret | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Tilstand unoccupied aktiveret | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Tilstand standby aktiveret | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Tilstand occupied aktiveret | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Tilstand tvungen ventilation aktiveret | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Tilstand Fra tekst | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Tilstand unoccupied tekst | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Tilstand standby tekst | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Tilstand occupied tekst | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Tilstand tvungen ventilation tekst | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Tilstand auto tekst | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menuvalg muligheder
|  |  | Menu titel tekst | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Tilstand varme aktiveret | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Tilstand køling aktiveret | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Tilstand auto aktiveret | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Tilstand varme tekst | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Tilstand køling tekst | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Tilstand auto tekst | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Aktuatorer
Tænd/sluk udgange
|  |  | Varme hysterese, rumtemperatur (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Køling hysterese, rumtemperatur (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, ekstra zone temperatur (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Ventilmotionering
|  |  | Test ventiler | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Varme interval (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Varme 2 interval (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Køle interval (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Køle 2 interval (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-over interval (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-vejsventil interval (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Varme varighed (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Varme 2 varighed (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Køle varighed (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Køle 2 varighed (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over varighed (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-vejsventil varighed (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoge indgange
Temperatur indgang
|  |  | Filtreringstid (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatur indgang 0-10 V
|  |  | Værdi ved 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Værdi ved 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 indgang
|  |  | Værdi ved 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Værdi ved 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtreringstid (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Fugtighed indgang
|  |  | Værdi ved 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Værdi ved 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtreringstid (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow indgang
|  |  | Værdi ved 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Værdi ved 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtreringstid (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC indgang
|  |  | Værdi ved 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Værdi ved 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtreringstid (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Sætpunkter
Rum sætpunkter
|  |  | Varme, occupied (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Køling, occupied (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Varme, standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Køling, standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Varme, unoccupied (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Køling, unoccupied (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frost beskyttelse (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Sætpunkts justering
|  |  | Maks. op-justering (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Maks. ned-justering (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Sætpunkts justering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Ekstra zone
|  |  | Ekstra zone sætpunkt (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 sætpunkt (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Fugtighed
|  |  | Fugtighed sætpunkt (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC sætpunkt | Setpoint for VOC control (RC_VOCSetpoint)
Kontroller indstillng
Rum
|  |  | P-bånd (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-time (s) | I-time for room PID controller (RC_RoomPIDItime)
Kaskade kontrol
|  |  | Styring aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskade faktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Maks. opvarmning temperatur (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. opvarmning temperatur (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Maks. kølling temperatur (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. køling temperatur (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frost beskyttelses temperatur (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Ekstra zone
|  |  | P-bånd (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-time (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-bånd (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-time (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Fugtighed
|  |  | P-bånd (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-time (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-bånd | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-time (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm indstilling
Rumtemperatur alarm
|  |  | Høj grænse (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Lav grænse (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2 niveaualarm
|  |  | Høj grænse (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Indgangs justeringer
UI1
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_1_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_1_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_1_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_1_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_2_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_2_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_2_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_2_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_2_offset)
Rumtemperatur
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_5_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_5_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_5_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_5_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_5_offset)
Rum fugtighed
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_6_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_6_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_6_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_6_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_6_offset)
VOC føler
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_7_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_7_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_7_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_7_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_7_offset)
CO2 føler
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Min. værdi | Scale for input (IoAnaIn_8_min_in)
|  |  | Maks. værdi | Scale for input (IoAnaIn_8_max_in)
|  |  | Justeret minimums værdi | Scale for input (IoAnaIn_8_min_out)
|  |  | Justeret maksimums værdi | Scale for input (IoAnaIn_8_max_out)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_8_offset)
Udgangs justeringer
UO1
|  |  | Min. værdi | Scale for output (IoAnaOut_1_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Min. værdi | Scale for output (IoAnaOut_2_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Min. værdi | Scale for output (IoAnaOut_3_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Min. værdi | Scale for output (IoAnaOut_4_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Manuel/Auto
Fjern indgangsværdier
Rumtemperatur
|  |  | Fjern indstilling | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Indstillet værdi (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Rumtemperatur (°C) | Room temperature (RC_RoomTemp)
Tilluft temperatur
|  |  | Fjern indstilling | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Indstillet værdi (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Tilluft temperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
Ekstra zone temperatur
|  |  | Fjern indstilling | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Indstillet værdi (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Ekstra zone temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperatur
|  |  | Fjern indstilling | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Indstillet værdi (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperatur (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-over temperatur
|  |  | Fjern indstilling | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Indstillet værdi (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over temperatur (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 niveau
|  |  | Fjern indstilling | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Indstillet værdi (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 niveau (ppm) | Room CO2 level (RC_CO2Level)
Rum fugtighed
|  |  | Fjern indstilling | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Indstillet værdi (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Rum fugtighed (%) | Relative humidity (RC_Humidity)
Luft flow
|  |  | Fjern indstilling | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Indstillet værdi | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Luft flow | Air flow (RC_AirFlow)
VOC indeks
|  |  | Fjern indstilling | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Indstillet værdi | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC indeks | VOC index (RC_VOC)
Tilstedeværelses detektering
|  |  | Fjern indstilling | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Indstillet værdi | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Tilstedeværelses detektering | Presence indication (RC_Presence)
Åbent vindue
|  |  | Fjern indstilling | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Indstillet værdi | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Åbent vindue | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Fjern indstilling | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Indstillet værdi | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Ekstern alarm (DI)
|  |  | Fjern indstilling | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Indstillet værdi | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Ekstern alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Fjern indstilling | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Indstillet værdi | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Fjern indstilling | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Indstillet værdi | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuel/Auto
Controller tilstand
|  |  | Controller tilstand | Current state (RC_ControllerState)
|  |  | Fjern tilstand indstilling | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Nedlukning | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Tvungen ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator styre kilde
|  |  | Ventilator styre kilde | Fan speed setting (RC_FanSelect)
Varme udgang
|  |  | Tilstand | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Varme udgang (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Tilstand | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Varme udgang | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Varme 2 udgang
|  |  | Tilstand | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Varme 2 udgang (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Tilstand | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Varme 2 udgang | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Køling udgang
|  |  | Tilstand | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Køling udgang (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Tilstand | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Køling udgang | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Køling 2 udgang
|  |  | Tilstand | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Køling 2 udgang (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Tilstand | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Køling 2 udgang | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV udgang
|  |  | Tilstand | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV udgang (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 udgang
|  |  | Tilstand | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 udgang (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over udgang
|  |  | Tilstand | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over udgang (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV udgang
|  |  | Tilstand | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV udgang (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-vejsventil udgang
|  |  | Tilstand | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Tilstand | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Indstillet værdi (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-vejsventil udgang (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Ekstra zone udgang
|  |  | Tilstand | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Ekstra zone udgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC ventilator styring
|  |  | Tilstand | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Indstillet værdi (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC ventilator styring (%) | Current EC fan speed (RC_ECFanSpeed)
CO2 kontrol udgang
|  |  | Tilstand | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Indstillet værdi (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 kontrol udgang (%) | CO2 control analog out (RC_CO2ControlAO)
Fugtning kontrol udgang
|  |  | Tilstand | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Fugtning kontrol udgang (%) | Humidify analog out (RC_HumidifyOutputAO)
Affugtning kontrol udgang
|  |  | Tilstand | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Indstillet værdi (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Affugtning kontrol udgang (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC kontrol udgang
|  |  | Tilstand | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Indstillet værdi (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC kontrol udgang (%) | VOC control analog out (RC_VOCControlAO)
Ekstra zone aktiv udgang
|  |  | Tilstand | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Ekstra zone aktiv udgang | Extra Zone active (RC_ExtraZoneActive)
Tvungen ventilation udgang
|  |  | Tilstand | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Tvungen ventilation udgang | Forced ventilation output (RC_ForcedVentDO)
Hardwarekontrol
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Indstillet værdi | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Indstillet værdi | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Indstillet værdi | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Indstillet værdi | Override value (IoAnaIn_2_override)
CO2-føler kalibrering
|  |  | Aktivér automatisk selv kalibrering | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatisk selv kalibrering mål CO2 ppm (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Kør CO2 føler tvungen genkalibrering | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Reference CO2 niveau for tvungen genkalibrering (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Sidste tvungne rekalibrerings resultat (-9999 = fejl) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Kør CO2 føler til fabriks standard | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relæ udgang
|  |  | Relæ status | Value set for output (IoDo_3_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Indstillet værdi | Override value (IoDo_3_override)
PIR føler
|  |  | PIR føler | Filtered value from sensor (IoDiIn_4_value)
|  |  | Tilstand | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Indstillet værdi | Override value (IoDiIn_4_override)
Enhed
Kontroller ID
Kontroller ID
|  |  | Navn | (ControllerName)
|  |  | Beskrivelse | Controller description (ControllerDescription)
|  |  | Lokation | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Port indstillinger
|  |  | Port 1 funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 baudhastighed | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 paritet | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus adresse | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP maks. masteradresse | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet enheds ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet enheds objektnavn | BACnet device object name (BACnetDeviceObjectName)
|  |  | Kodeord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth funktion | Function for BLE button (BleButtonMode)
|  |  | Sluk efter (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Kommunikations fejl
|  |  | Fejl handling | Offline function (RC_OfflineFunction)
|  |  | Timeout (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback tilstand | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Nulstil
Nulstil
|  |  | Genstart kontroller | Write to this register will trigger resets with different reset reasons (product_reset)

## de
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Übersicht
System
|  |  | Regler | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus-Adresse | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP Adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet Geräte-ID | BACnet device ID (BACnetDeviceID)
|  |  | Sammelalarm | Sum Alarm (RC_SumAlarm)
Raum
|  |  | Reglerstatus | Current state (RC_ControllerState)
|  |  | Betriebsmodus | Current controller mode (RC_ControllerMode)
|  |  | Raumtemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Zulufttemperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Raumsollwert (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sollwertanpassung (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC-Ventilatordrehzahl (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2-Gehalt (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Raumfeuchte (%) | Relative humidity (RC_Humidity)
|  |  | VOC-Index | VOC index (RC_VOC)
|  |  | Präsenzerkennung | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Extrazone
|  |  | Extrazone Temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extrazone Sollwert (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extrazone aktiver Ausgang | Extra Zone active (RC_ExtraZoneActive)
Istwerte
Raumregler Sequenz
|  |  | Sequenz 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequenz 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequenz 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Istwerte
|  |  | Betriebsmodus | Current controller mode (RC_ControllerMode)
|  |  | Raumtemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Raumsollwert (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sollwertanpassung (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Heizanforderung (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Kühlanforderung (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Ausgang Heizen (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Ausgang Heizen 2 (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Ausgang Kühlen (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Ausgang Kühlen 2 (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Ausgang VVS (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | Ausgang VVS 2 (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-Over Temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-Over Status | Change-over status (RC_ChangeOverState)
|  |  | Ausgang Change-Over (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-Over VVS Temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-Over VVS Status | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Ausgang Change-Over VVS (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Ausgang 6-Wege-Ventil (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2-Gehalt (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2-Sollwert (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Relaisausgang
|  |  | Status Relais | Value set for output (IoDo_3_value)
|  |  | Quelle 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Deaktivierungsgrenze | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Aktivierungsgrenze | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Quelle 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Deaktivierungsgrenze | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Aktivierungsgrenze | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Quelle 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Deaktivierungsgrenze | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Aktivierungsgrenze | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Quelle 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Deaktivierungsgrenze | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Aktivierungsgrenze | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timer-Status | Current timer state (rt_exttime_state)
|  |  | Aktiver Timer-Wert | Time remaining (rt_exttime_timeleft)
Eingänge/Ausgänge
Universaleingänge
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universalausgänge
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analogausgänge
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne Fühler
|  |  | Raumtemperatur (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2-Fühler (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Feuchtefühler (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC-Sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR-Sensor | Filtered value from sensor (IoDiIn_4_value)
Alarme
Alarme
|  |  | Sammelalarm | Sum Alarm (RC_SumAlarm)
|  |  | Fühlerfehler | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hohe Raumtemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Niedrige Raumtemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hoher CO2-Gehalt | High CO2 alarm (RC_AlarmCO2High)
|  |  | Externer Alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Ausgang im Handbetrieb | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Fehlercode Temperaturfühler | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Fehlercode Feuchtefühler | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Fehlercode VOC-Sensor | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Fehlercode CO2-Fühler | Detailed fault description (IoAnaIn_8_errorFlags)
Info
Regler-ID
|  |  | Seriennummer | (SerialNumberString)
|  |  | Name | (ControllerName)
|  |  | Beschreibung | Controller description (ControllerDescription)
|  |  | Standort | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Konfiguration
Reglerfunktionen
Raumregler Sequenz
|  |  | Sequenz 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequenz 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequenz 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Heizen
|  |  | Max.-Grenze (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min.-Grenze (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Ventilator Ausschaltverzögerung bei Elektroerhitzer | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Change-Over Status folgen | Heat1 included in change-over function (RC_Heat1InChangeOver)
Heizen 2
|  |  | Max.-Grenze (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min.-Grenze (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Ventilator Ausschaltverzögerung bei Elektroerhitzer | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Change-Over Status folgen | Heat2 included in change-over function (RC_Heat2InChangeOver)
Kühlen
|  |  | Max.-Grenze (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min.-Grenze (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Bei Zwangslüftung auf max. einstellen | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Change-Over Status folgen | Cool1 included in change-over function (RC_Cool1InChangeOver)
Kühlen 2
|  |  | Max.-Grenze (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min.-Grenze (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Bei Zwangslüftung auf max. einstellen | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Change-Over Status folgen | Cool2 included in change-over function (RC_Cool2InChangeOver)
VVS
|  |  | Max.-Grenze (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min.-Grenze, Aus (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min.-Grenze, Nicht belegt (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min.-Grenze, Standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min.-Grenze, Belegt (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max.-Grenze beim Heizen (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Change-Over Status folgen | VAV1 included in change-over function (RC_VAV1InChangeOver)
VVS 2
|  |  | Max.-Grenze (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min.-Grenze, Aus (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min.-Grenze, Nicht belegt (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min.-Grenze, Standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min.-Grenze, Belegt (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max.-Grenze beim Heizen (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Change-Over Status folgen | VAV2 included in change-over function (RC_VAV2InChangeOver)
VVS-Regelquelle
|  |  | Anforderung Kühlen | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2-Gehalt | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-Index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Feuchte | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-Over
|  |  | Max.-Grenze (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min.-Grenze (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Betriebsmodus | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-Over Temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Heizhysterese (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Kühlhysterese (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Verzögerungszeit Ventil (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-Over VVS
|  |  | Max.-Grenze (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min.-Grenze, Aus (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min.-Grenze, Nicht belegt (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min.-Grenze, Standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min.-Grenze, Belegt (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Betriebsmodus | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-Over Temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Heizhysterese (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Kühlhysterese (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Verzögerungszeit Ventil (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-Wege Ventil
|  |  | Seq 1 voll offen (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Seq 1 Start Öffnen (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Seq 2 voll offen (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Seq 2 Start Öffnen (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Mittelpunkt (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Mittelpunkt Hysterese (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sequenz-Reihenfolge | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Change-Over Status folgen | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Reglerstatus
|  |  | Voreingestellter Status | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Abschaltstatus | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Status Offenes Fenster | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Zeit im Status Zwangslüftung (min) | Bypass time (minutes) (RC_BypassTime)
Zwangslüftung
|  |  | Aktiviert wenn | Forced ventilation function (RC_ForcedVentMode)
|  |  | Startgrenze (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Präsenzerkennung
|  |  | Status Präsenz | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Verzögerung aktiv (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Verzögerung inaktiv (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 Aktivierung | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2-Gehalt (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 Hysterese (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Internen PIR für Präsenz verwenden | Use internal PID sensor for presence detection (RC_PIDPresence)
Extrazone
Extrazone
|  |  | Extrazone Funktion | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Deaktiviert unter Status | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Deaktivieren bei Abweichung Hauptzonenmodus von Funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min.-Grenze (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max.-Grenze (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Eingänge/Ausgänge
Universaleingänge
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universalausgänge
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 Pulsdauer thermischer Antrieb (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 Stellsignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 Pulsdauer thermischer Antrieb (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 Stellsignal | Unit converter (IoAnaOut_2_unit)
Analogausgänge
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 Stellsignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 Stellsignal | Unit converter (IoAnaOut_4_unit)
Ventilatorregelung
Ventilator Regelquelle
|  |  | Raumregler | Select fan control mode (RC_FanControlMode)
|  |  | CO2-Gehalt | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Feuchte | Fan is controlled by humidity output (RC_FanControlHumidity)
EC-Ventilatorregelung
|  |  | Ventilatorstufe bei keinem Bedarf | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Aus unterhalb Bedarf (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese Reduzierung Ventilatorstufe (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start Ventilatorstufe (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. Ventilatorstufe im Automatikbetrieb (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Zwangslüftung Ventilatorstufe | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Zwangslüftung Ventilatorstufe (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Stufe 1 Ausgang (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Stufe 2 Ausgang (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Stufe 3 Ausgang (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Schimmelschutzfunktion | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Ventilator Kickstart
|  |  | Kickstart Dauer (s) | Fan kick start time (RC_FanKickStartTime)
Ventilator Ausschaltverzögerung
|  |  | Ausschaltverzögerungszeit (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimale Ventilatorstufe | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilator Boost
|  |  | Betriebsmodus | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost Dauer (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-Band | Fan boost P band (RC_FanBoostPBand)
Display und Menüs
Display
|  |  | Startbildschirm | What to display during device startup (DisplayStartupMode)
|  |  | Anzeigemodus | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Abwechselnd Temp./CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Sollwertmodus | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | CO2 auf den nächsten Wert runden | Min step for CO2 value (RC_CO2Step)
|  |  | Volle Helligkeit (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dimmen Timeout, 0 = Immer voll (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Helligkeit gedimmt (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Aus Timeout, 0 = Nie aus (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Anzuzeigende Werte
Timer
|  |  | Anzeigemodus | How to show the timer in the display (rt_exttime_mode)
|  |  | Animation | Show animation in timer view (rt_exttime_animate)
|  |  | LED einschalten, wenn aktiv | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Schrittweite in Minuten (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Anzahl der Schritte | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Aktueller Timer-Wert (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timer-Status | Current timer state (rt_exttime_state)
Benutzerdefinierte Texte
|  |  | Anzeigemodus | When to show the custom text (rt_text_visability)
|  |  | Anzeigemodus | Single or dual row text in display (rt_text_mode)
|  |  | Scrollmodus | Scroll mode (rt_text_display_scroll_mode)
|  |  | Schriftart | What font to use for the display text (rt_text_font)
|  |  | Scrollverzögerung (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Benutzerdefinierter Text Timer-Wert (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Benutzerdefinierter Text Zeile 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Benutzerdefinierter Text Zeile 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Benutzerdefinierter Text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Benutzerdefinierter Text 2 | String to show on row 2 in the display (rt_text_row_2)
LED-Anzeige
|  |  | Helligkeit (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED-Anzeige | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gelbe LED CO2-Gehalt (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rote LED CO2-Gehalt (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menü
|  |  | Sollwertanpassung | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Status Menüseite | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-Over Menüseite | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator Menüseite | Enable Fan menu page (App_EnableMenuFan)
|  |  | Zwangslüftung Menüseite | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Zwangslüftung Nachlauf | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Feuchte Menüseite | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 Menüseite | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC Menüseite | Enable VOC menu page (App_EnableMenuVOC)
Menüoptionen Status
|  |  | Menü Titeltext | Mode menu title (App_ModeMenuTitle)
|  |  | Status Aus aktivieren | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Status Nicht belegt aktivieren | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Status Standby aktivieren | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Status Belegt aktivieren | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Status Zwangslüftung aktivieren | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Status Aus Text | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Status Nicht belegt Text | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Status Standby Text | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Status Belegt Text | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Status Zwangslüftung Text | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Status Auto Text | Mode menu Auto state text (App_ModeMenuAutoText)
Menüoptionen Change-Over
|  |  | Menü Titeltext | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Modus Heizen aktivieren | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Modus Kühlen aktivieren | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Modus Auto aktivieren | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Modus Heizen Text | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Modus Kühlen Text | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Modus Auto Text | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Stellantriebe
Ein/Aus-Ausgänge
|  |  | Heizhysterese, Raumtemperatur (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Kühlhysterese, Raumtemperatur (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, Extrazone Temperatur (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Blockierschutz Ventil
|  |  | Typ Blockierschutz | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Heizintervall (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Heizintervall 2 (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Kühlintervall (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Kühlintervall 2 (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-Over Intervall (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-Wege-Ventil Intervall (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Heizdauer (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Heizdauer 2 (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Kühldauer (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Kühldauer 2 (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-Over Dauer (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-Wege-Ventil Dauer (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analogeingänge
Temperatureingang
|  |  | Filterzeit (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatureingang 0-10 V
|  |  | Wert bei 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Wert bei 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2-Eingang
|  |  | Wert bei 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Wert bei 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filterzeit (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Feuchteeingang
|  |  | Wert bei 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Wert bei 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filterzeit (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Volumenstromeingang
|  |  | Wert bei 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Wert bei 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filterzeit (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC-Eingang
|  |  | Wert bei 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Wert bei 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filterzeit (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Sollwerte
Raumsollwerte
|  |  | Heizen, Belegt (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Kühlen, Belegt (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Heizen, Standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Kühlen, Standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Heizen, Nicht belegt (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Kühlen, Nicht belegt (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frostschutz (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Sollwertanpassung
|  |  | Max. Anpassung nach oben (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max. Anpassung nach unten (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Sollwertanpassung (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extrazone
|  |  | Extrazone Sollwert (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2-Sollwert (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Feuchte
|  |  | Feuchte Sollwert (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC-Sollwert | Setpoint for VOC control (RC_VOCSetpoint)
Reglereinstellungen
Raum
|  |  | P-Band (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-Zeit (s) | I-time for room PID controller (RC_RoomPIDItime)
Kaskadenregelung
|  |  | Regelung aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskadenfaktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. Heiztemperatur (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. Heiztemperatur (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. Kühltemperatur (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. Kühltemperatur (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frostschutztemperatur (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extrazone
|  |  | P-Band (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-Zeit (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-Band (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-Zeit (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Feuchte
|  |  | P-Band (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-Zeit (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-Band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-Zeit (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Alarmeinstellungen
Raumtemperatur Alarm
|  |  | Oberer Grenzwert (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Unterer Grenzwert (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2-Gehalt Alarm
|  |  | Oberer Grenzwert (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Anpassungen Eingänge
UI1
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_1_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_1_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_1_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_1_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_2_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_2_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_2_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_2_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_2_offset)
Raumtemperatur
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_5_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_5_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_5_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_5_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_5_offset)
Raumfeuchte
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_6_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_6_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_6_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_6_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_6_offset)
VOC-Sensor
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_7_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_7_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_7_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_7_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_7_offset)
CO2-Fühler
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Minimalwert | Scale for input (IoAnaIn_8_min_in)
|  |  | Maximalwert | Scale for input (IoAnaIn_8_max_in)
|  |  | Angepasster Minimalwert | Scale for input (IoAnaIn_8_min_out)
|  |  | Angepasster Maximalwert | Scale for input (IoAnaIn_8_max_out)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_8_offset)
Anpassungen Ausgänge
UO1
|  |  | Minimalwert | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimalwert | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimalwert | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimalwert | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Hand/Auto
Ferneingabewerte
Raumtemperatur
|  |  | Ferneinstellung | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Einstellwert (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Raumtemperatur (°C) | Room temperature (RC_RoomTemp)
Zulufttemperatur
|  |  | Ferneinstellung | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Einstellwert (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Zulufttemperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
Extrazone Temperatur
|  |  | Ferneinstellung | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Einstellwert (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extrazone Temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-Over Temperatur
|  |  | Ferneinstellung | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Einstellwert (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-Over Temperatur (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-Over VVS Temperatur
|  |  | Ferneinstellung | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Einstellwert (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-Over VVS Temperatur (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2-Gehalt
|  |  | Ferneinstellung | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Einstellwert (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2-Gehalt (ppm) | Room CO2 level (RC_CO2Level)
Raumfeuchte
|  |  | Ferneinstellung | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Einstellwert (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Raumfeuchte (%) | Relative humidity (RC_Humidity)
Volumenstrom
|  |  | Ferneinstellung | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Einstellwert | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Volumenstrom | Air flow (RC_AirFlow)
VOC-Index
|  |  | Ferneinstellung | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Einstellwert | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-Index | VOC index (RC_VOC)
Präsenzerkennung
|  |  | Ferneinstellung | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Einstellwert | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Präsenzerkennung | Presence indication (RC_Presence)
Offenes Fenster
|  |  | Ferneinstellung | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Einstellwert | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Offenes Fenster | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Ferneinstellung | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Einstellwert | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Externer Alarm (DI)
|  |  | Ferneinstellung | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Einstellwert | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Externer Alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-Over DI
|  |  | Ferneinstellung | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Einstellwert | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-Over DI | Change-over digital input (RC_DIChangeOver)
Change-Over VVS DI
|  |  | Ferneinstellung | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Einstellwert | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-Over VVS DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Hand/Auto
Reglerstatus
|  |  | Reglerstatus | Current state (RC_ControllerState)
|  |  | Fernstatuseinstellung | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Ausschalten | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Zwangslüftung | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator Regelquelle
|  |  | Ventilator Regelquelle | Fan speed setting (RC_FanSelect)
Ausgang Heizen
|  |  | Betriebsmodus | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Ausgang Heizen (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Betriebsmodus | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Ausgang Heizen | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Ausgang Heizen 2
|  |  | Betriebsmodus | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Ausgang Heizen 2 (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Betriebsmodus | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Ausgang Heizen 2 | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Ausgang Kühlen
|  |  | Betriebsmodus | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Ausgang Kühlen (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Betriebsmodus | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Ausgang Kühlen | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Ausgang Kühlen 2
|  |  | Betriebsmodus | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Ausgang Kühlen 2 (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Betriebsmodus | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Ausgang Kühlen 2 | Room control Cool2 output digital (RC_RoomCool2OutputDO)
Ausgang VVS
|  |  | Betriebsmodus | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | Ausgang VVS (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
Ausgang VVS 2
|  |  | Betriebsmodus | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | Ausgang VVS 2 (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Ausgang Change-Over
|  |  | Betriebsmodus | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Ausgang Change-Over (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Ausgang Change-Over VVS
|  |  | Betriebsmodus | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Einstellwert (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Ausgang Change-Over VVS (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Ausgang 6-Wege-Ventil
|  |  | Betriebsmodus | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Betriebsmodus | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Einstellwert (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Ausgang 6-Wege-Ventil (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extrazone Ausgang
|  |  | Betriebsmodus | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Einstellwert (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extrazone Ausgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC-Ventilatorregelung
|  |  | Betriebsmodus | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Einstellwert (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC-Ventilatorregelung (%) | Current EC fan speed (RC_ECFanSpeed)
CO2 Regelausgang
|  |  | Betriebsmodus | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Einstellwert (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 Regelausgang (%) | CO2 control analog out (RC_CO2ControlAO)
Feuchte Regelausgang
|  |  | Betriebsmodus | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Einstellwert (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Feuchte Regelausgang (%) | Humidify analog out (RC_HumidifyOutputAO)
Entfeuchter Regelausgang
|  |  | Betriebsmodus | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Einstellwert (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Entfeuchter Regelausgang (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC Regelausgang
|  |  | Betriebsmodus | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Einstellwert (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC Regelausgang (%) | VOC control analog out (RC_VOCControlAO)
Extrazone aktiver Ausgang
|  |  | Betriebsmodus | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extrazone aktiver Ausgang | Extra Zone active (RC_ExtraZoneActive)
Zwangslüftung Ausgang
|  |  | Betriebsmodus | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Zwangslüftung Ausgang | Forced ventilation output (RC_ForcedVentDO)
Hardwaresteuerung
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Einstellwert | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Einstellwert | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Einstellwert | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Einstellwert | Override value (IoAnaIn_2_override)
Kalibrierung CO2-Fühler
|  |  | Automatische Selbstkalibrierung aktivieren | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatische Selbstkalibrierung Ziel CO2 ppm (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | CO2-Fühler erzwungene Neukalibrierung | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | CO2-Referenzwert für erzwungene Neukalibrierung (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Ergebnis letzte erzwungene Neukalibrierung (-9999=Fehler) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | CO2-Fühler auf Werkseinstellung zurücksetzen | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relaisausgang
|  |  | Status Relais | Value set for output (IoDo_3_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Einstellwert | Override value (IoDo_3_override)
PIR-Sensor
|  |  | PIR-Sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Einstellwert | Override value (IoDiIn_4_override)
Gerät
Regler-ID
Regler-ID
|  |  | Name | (ControllerName)
|  |  | Beschreibung | Controller description (ControllerDescription)
|  |  | Standort | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Porteinstellungen
|  |  | Port 1 Funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 Baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 Parität | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus-Adresse | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP Adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP Max Master Adresse | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet Geräte-ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet Gerät Objektname | BACnet device object name (BACnetDeviceObjectName)
|  |  | Passwort | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-Funktion | Function for BLE button (BleButtonMode)
|  |  | Ausschalten nach (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Kommunikationsausfall
|  |  | Fehler | Offline function (RC_OfflineFunction)
|  |  | Timeout (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback Status | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Zurücksetzen
Zurücksetzen
|  |  | Regler Neustart | Write to this register will trigger resets with different reset reasons (product_reset)

## fr
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Tableau de bord
Vue d’ensemble
Système
|  |  | Régulateur | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Adresse Modbus | Active Modbus unit ID (ModbusUnitID)
|  |  | Adresse BACnet MSTP | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | ID bas BACnet | BACnet device ID (BACnetDeviceID)
|  |  | Total des alarmes | Sum Alarm (RC_SumAlarm)
Ambiance
|  |  | État du régulateur | Current state (RC_ControllerState)
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Température d’ambiance (°C) | Room temperature (RC_RoomTemp)
|  |  | Température de soufflage (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Consigne d’ambiance (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Décalage de consigne (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Vitesse du ventilateur EC (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | Niveau de CO2 (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Humidité ambiante (%) | Relative humidity (RC_Humidity)
|  |  | Indice de COV | VOC index (RC_VOC)
|  |  | Détection de présence | Presence indication (RC_Presence)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Zone supplémentaire
|  |  | Température de la zone supplémentaire (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Consigne zone supplémentaire (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Sortie zone supplémentaire active | Extra Zone active (RC_ExtraZoneActive)
Valeurs réelles
Séquence de contrôle d'ambiance
|  |  | Séquence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Séquence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Séquence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Valeurs réelles
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Température d’ambiance (°C) | Room temperature (RC_RoomTemp)
|  |  | Consigne d’ambiance (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Décalage de consigne (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Demande de chauffage (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Demande de refroidissement (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Sortie chauffage (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Sortie chauffage 2 (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Sortie refroidissement (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Sortie refroidissement 2 (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Sortie VAV (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | Sortie VAV 2 (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Température de change-over | Changeover temperature (RC_ChangeOverTemp)
|  |  | État du change-over | Change-over status (RC_ChangeOverState)
|  |  | Sortie change-over (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Température de change-over VAV | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | État du change-ove VAV | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Sortie VAV change-over (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Sortie vanne 6 voies (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | Niveau de CO2 (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Consigne CO2 (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Sortie relais
|  |  | État du relais | Value set for output (IoDo_3_value)
|  |  | Source 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Désactiver la limite | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Activer la limite | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Source 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Désactiver la limite | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Activer la limite | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Source 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Désactiver la limite | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Activer la limite | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Source 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Désactiver la limite | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Activer la limite | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | État du timer | Current timer state (rt_exttime_state)
|  |  | Valeur active du timer | Time remaining (rt_exttime_timeleft)
Entrées/Sorties
Entrées universelles
|  |  | UI1 : | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1 : | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2 : | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2 : | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Sorties universelles
|  |  | UO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1 : | Value set for output (IoDo_1_value)
|  |  | UO2 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2 : | Value set for output (IoDo_2_value)
Sorties analogiques
|  |  | AO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Sondes internes
|  |  | Température d’ambiance (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | Sonde de CO2 (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Sonde HR (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | Sonde COV | Filtered value from sensor (IoAnaIn_7_value)
|  |  | Capteur PIR | Filtered value from sensor (IoDiIn_4_value)
Alarmes
Alarmes
|  |  | Total des alarmes | Sum Alarm (RC_SumAlarm)
|  |  | Erreur sonde | Sensor error alarm (RC_AlarmSensorError)
|  |  | Température ambiante haute | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Température ambiante basse | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Niveau de CO2 élevé | High CO2 alarm (RC_AlarmCO2High)
|  |  | Alarme externe (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Sortie en mode manuel | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Code d’erreur de la sonde de température | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Code d’erreur de la sonde d’humidité | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Code d'erreur de la sonde de COV | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Code d'erreur de la sonde de CO2 | Detailed fault description (IoAnaIn_8_errorFlags)
À propos de…
Identification du régulateur
|  |  | Nº de série | (SerialNumberString)
|  |  | Nom | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Emplacement | Controller location (ControllerLocation)
|  |  | Projet | (ControllerProject)
Configuration
Fonctions de contrôle
Séquence de contrôle d'ambiance
|  |  | Séquence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Séquence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Séquence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Chaleur
|  |  | Limite max. (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Limite min. (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Temporisation d’arrêt du ventilateur batterie électrique | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Suivre l'état du change-over | Heat1 included in change-over function (RC_Heat1InChangeOver)
Chaleur 2
|  |  | Limite max. (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Limite min. (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Temporisation d’arrêt du ventilateur batterie électrique | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Suivre l'état du change-over | Heat2 included in change-over function (RC_Heat2InChangeOver)
Froid
|  |  | Limite max. (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Limite min. (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Régler au maximum en mode ventilation forcée | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Suivre l'état du change-over | Cool1 included in change-over function (RC_Cool1InChangeOver)
Froid 2
|  |  | Limite max. (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Limite min. (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Régler au maximum en mode ventilation forcée | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Suivre l'état du change-over | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Limite max. (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Limite min., Arrêt (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Limite min., inoccupé (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Limite min., standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Limite min., occupé (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Limite min., ventilation forcée (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Limite max. en chauffage (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Suivre l'état du change-over | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Limite max. (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Limite min., Arrêt (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Limite min., inoccupé (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Limite min., standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Limite min., occupé (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Limite min., ventilation forcée (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Limite max. en chauffage (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Suivre l'état du change-over | VAV2 included in change-over function (RC_VAV2InChangeOver)
Source de commande VAV
|  |  | Demande de refroidissement | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | Niveau de CO2 | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | Indice de COV | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Humidité | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Limite max. (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Limite min. (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Mode | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Température de change-over (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Hystérésis de chauffage (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Hystérésis de refroidissement (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Temporisation vanne (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Limite max. (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Limite min., Arrêt (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Limite min., inoccupé (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Limite min., standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Limite min., occupé (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Limite min., ventilation forcée (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Mode | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Température de change-over (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Hystérésis de chauffage (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Hystérésis de refroidissement (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Temporisation vanne (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
Vanne 6 voies
|  |  | Séq 1 totalement ouvert (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Séq 1 début ouverture (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Séq 2 totalement ouvert (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Séq 2 début ouverture (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Point central (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Hystérésis du point central (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Ordre séquence | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Suivre l'état du change-over | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
État du régulateur
|  |  | État préréglé | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | État à l'arrêt | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | État fenêtre ouverte | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Temps en mode ventilation forcée (min) | Bypass time (minutes) (RC_BypassTime)
Ventilation forcée
|  |  | Actif quand | Forced ventilation function (RC_ForcedVentMode)
|  |  | Limite de démarrage (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Détection de présence
|  |  | État présence | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Temporisation activation (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Temporisation désactivation (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | Activation CO2 | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | Niveau de CO2 (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | Hystérésis CO2 (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Utiliser le PIR interne pour la présence | Use internal PID sensor for presence detection (RC_PIDPresence)
Zone supplémentaire
Zone supplémentaire
|  |  | Fonction zone supplémentaire | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Désactivé en dessous de l’état | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Désactiver si le mode de zone principale diffère de la fonction | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Limite min. (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Limite max. (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Entrées/Sorties
Entrées universelles
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NF/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NF/NO | Invert logic signal (IoDiIn_2_invert)
Sorties universelles
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | Temps de cycle vanne thermique UO1 (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NF/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | Signal de contrôle UO1 | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | Temps de cycle vanne thermique UO2 (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NF/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | Signal de contrôle UO2 | Unit converter (IoAnaOut_2_unit)
Sorties analogiques
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | Signal de contrôle AO1 | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | Signal de contrôle AO2 | Unit converter (IoAnaOut_4_unit)
Contrôle ventilateurs
Source de contrôle ventilateur
|  |  | Contrôleur d’ambiance | Select fan control mode (RC_FanControlMode)
|  |  | Niveau de CO2 | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Humidité | Fan is controlled by humidity output (RC_FanControlHumidity)
Commande du ventilateur EC
|  |  | Vitesse sans demande | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Arrêt en dessous de la demande (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hystérésis pour diminution de la vitesse du ventilateur (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Vitesse de démarrage (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Vitesse max. en mode automatique (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Vitesse ventilation forcée | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Vitesse ventilation forcée (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Sortie vitesse 1 (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Sortie vitesse 2 (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Sortie vitesse 3 (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Protection moisissure | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Démarrage rapide ventilateur
|  |  | Durée du démarrage rapide (s) | Fan kick start time (RC_FanKickStartTime)
Délai d’arrêt ventilateur
|  |  | Délai d’arrêt (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Vitesse minimale | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Boost ventilateur
|  |  | Mode | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Durée de boost (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | Bande proportionnelle | Fan boost P band (RC_FanBoostPBand)
Affichage et menus
Affichage
|  |  | Écran d'accueil | What to display during device startup (DisplayStartupMode)
|  |  | Mode d’affichage | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Alternance Température/CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Mode de consigne | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Arrondir la valeur de CO2 au plus proche | Min step for CO2 value (RC_CO2Step)
|  |  | Luminosité totale (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Temporisation gradation, 0 = Toujours totale (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Luminosité réduite (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Temporisation, 0 = Jamais désactivé (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Valeurs à afficher
Timer
|  |  | Mode d'affichage | How to show the timer in the display (rt_exttime_mode)
|  |  | Animation | Show animation in timer view (rt_exttime_animate)
|  |  | Allumer la LED si actif | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Taille de l’incrément en minutes (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Nombre d'étages | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Valeur actuelle du timer (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | État du timer | Current timer state (rt_exttime_state)
Textes personnalisés
|  |  | Mode d’affichage | When to show the custom text (rt_text_visability)
|  |  | Mode d'affichage | Single or dual row text in display (rt_text_mode)
|  |  | Mode défilement | Scroll mode (rt_text_display_scroll_mode)
|  |  | Police | What font to use for the display text (rt_text_font)
|  |  | Délai de défilement (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Valeur de timer de texte personnalisé (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Ligne de texte personnalisé 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Ligne de texte personnalisé 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Texte personnalisé 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Texte personnalisé 2 | String to show on row 2 in the display (rt_text_row_2)
LED d'indication
|  |  | Luminosité (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Indication LED CO2 | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | LED jaune Niveau de CO2 (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | LED rouge Niveau de CO2 (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menu
|  |  | Réglage de la consigne | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Page de menu Mode | Enable Mode menu page (App_EnableMenuMode)
|  |  | Page de menu Change-over | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Page de menu Ventilateur | Enable Fan menu page (App_EnableMenuFan)
|  |  | Page de menu Ventilation forcée | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Relance ventilation forcée | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Page de menu Humidité | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | Page de menu CO2 | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | Page de menu COV | Enable VOC menu page (App_EnableMenuVOC)
Options du menu Mode
|  |  | Texte du menu Titre | Mode menu title (App_ModeMenuTitle)
|  |  | Activation du mode Off | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Activation du mode Inoccupé | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Activation du mode Standby | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Activation du mode Occupé | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Activation du mode Ventilation forcée | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Texte du mode Off | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Texte du mode Inoccupé | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Texte du mode Standby | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Texte du mode Occupé | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Texte du mode Ventilation forcée | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Texte du mode Automatique | Mode menu Auto state text (App_ModeMenuAutoText)
Options du menu Change-over
|  |  | Texte du menu Titre | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | État Chauffage activé | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | État Refroidissement activé | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | État Auto activé | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Texte de l'état Chauffage | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Texte de l'état Refroidissement | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Texte de l'état Auto | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Actionneurs
Sorties On/Off
|  |  | Hystérésis de chauffage, température ambiante (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Hystérésis de refroidissement, température ambiante (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hystérésis, température de zone supplémentaire (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Exercice de vanne
|  |  | Exercice de vannes | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Intervalle de chauffage (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Intervalle chauffage 2 (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Intervalle de refroidissement (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Intervalle de refroidissement 2 (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Intervalle change-over (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Intervalle vanne 6 voies (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Durée chauffage (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Durée chauffage 2 (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Durée refroidissement (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Durée refroidissement 2 (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Durée change-over (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | Durée vanne 6 voies (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Entrées analogiques
Entrée température
|  |  | Temps de filtrage (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Entrée température 0-10V
|  |  | Valeur à 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Valeur à 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
Entrée CO2
|  |  | Valeur à 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Valeur à 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Temps de filtrage (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Entrée humidité
|  |  | Valeur à 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Valeur à 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Temps de filtrage (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Entrée débit
|  |  | Valeur à 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Valeur à 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Temps de filtrage (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
Entrée COV
|  |  | Valeur à 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Valeur à 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Temps de filtrage (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Points de consigne
Consignes d’ambiance
|  |  | Chauffage, occupé (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Refroidissement, occupé (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Chauffage, standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Refroidissement, standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Chauffage, inoccupé (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Refroidissement, inoccupé (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Protection antigel (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Décalage de consigne
|  |  | Réglage max. vers le haut (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Réglage max. vers le bas (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Décalage de consigne (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Zone supplémentaire
|  |  | Consigne zone supplémentaire (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | Consigne CO2 (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Humidité
|  |  | Consigne humidité (%) | Setpoint Humidity control (RC_HumiditySetpoint)
COV
|  |  | Consigne COV | Setpoint for VOC control (RC_VOCSetpoint)
Réglages du régulateur
Ambiance
|  |  | Bande proportionnelle (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | Temps d’intégration (s) | I-time for room PID controller (RC_RoomPIDItime)
Contrôle en cascade
|  |  | Contrôle activé | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Facteur de cascade | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Température de chauffage max. (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Température de chauffage min. (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Température de refroidissement max. (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Température de refroidissement min. (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Température protection antigel (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Zone supplémentaire
|  |  | Bande proportionnelle (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | Temps d’intégration (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | Bande proportionnelle (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | Temps d’intégration (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Humidité
|  |  | Bande proportionnelle (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | Temps d’intégration (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
COV
|  |  | Bande proportionnelle | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | Temps d’intégration (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Réglage des alarmes
Alarme température ambiante
|  |  | Limite haute (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Limite basse (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Alarme de niveau de CO2
|  |  | Limite haute (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Réglages des entrées
UI1
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_1_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_1_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_1_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_1_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_2_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_2_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_2_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_2_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_2_offset)
Température d’ambiance
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_5_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_5_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_5_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_5_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_5_offset)
Humidité ambiante
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_6_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_6_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_6_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_6_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_6_offset)
Sonde COV
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_7_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_7_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_7_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_7_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_7_offset)
Sonde de CO2
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Valeur minimale | Scale for input (IoAnaIn_8_min_in)
|  |  | Valeur maximale | Scale for input (IoAnaIn_8_max_in)
|  |  | Valeur minimale ajustée | Scale for input (IoAnaIn_8_min_out)
|  |  | Valeur maximale ajustée | Scale for input (IoAnaIn_8_max_out)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_8_offset)
Réglages de sortie
UO1
|  |  | Valeur minimale | Scale for output (IoAnaOut_1_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_1_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Valeur minimale | Scale for output (IoAnaOut_2_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_2_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Valeur minimale | Scale for output (IoAnaOut_3_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_3_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Valeur minimale | Scale for output (IoAnaOut_4_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_4_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Manuel/Auto
Valeurs des entrées distantes
Température d’ambiance
|  |  | Commande à distance | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Valeur réglée (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Température d’ambiance (°C) | Room temperature (RC_RoomTemp)
Température de soufflage
|  |  | Commande à distance | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Valeur réglée (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Température de soufflage (°C) | Supply air temperature (RC_SupplyAirTemp)
Température de la zone supplémentaire
|  |  | Commande à distance | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Valeur réglée (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Température de la zone supplémentaire (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Température de change-over
|  |  | Commande à distance | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Valeur réglée (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Température de change-over (°C) | Changeover temperature (RC_ChangeOverTemp)
Température de change-over VAV
|  |  | Commande à distance | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Valeur réglée (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Température de change-over VAV (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
Niveau de CO2
|  |  | Commande à distance | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Valeur réglée (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | Niveau de CO2 (ppm) | Room CO2 level (RC_CO2Level)
Humidité ambiante
|  |  | Commande à distance | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Valeur réglée (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Humidité ambiante (%) | Relative humidity (RC_Humidity)
Débit d’air
|  |  | Commande à distance | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Valeur réglée | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Débit d’air | Air flow (RC_AirFlow)
Indice de COV
|  |  | Commande à distance | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Valeur réglée | Remote setting of VOC index (RC_VOCRemote)
|  |  | Indice de COV | VOC index (RC_VOC)
Détection de présence
|  |  | Commande à distance | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Valeur réglée | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Détection de présence | Presence indication (RC_Presence)
Fenêtre ouverte
|  |  | Commande à distance | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Valeur réglée | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Fenêtre ouverte | Open window indication (RC_DIOpenWindow)
Condensation
|  |  | Commande à distance | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Valeur réglée | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Alarme externe (DI)
|  |  | Commande à distance | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Valeur réglée | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Alarme externe (DI) | Digital input alarm (RC_AlarmDI)
DI Change-over
|  |  | Commande à distance | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Valeur réglée | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | DI Change-over | Change-over digital input (RC_DIChangeOver)
DI Change-over VAV
|  |  | Commande à distance | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Valeur réglée | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | DI Change-over VAV | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuel/Auto
État du régulateur
|  |  | État du régulateur | Current state (RC_ControllerState)
|  |  | Réglage commande à distance | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Arrêt | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Ventilation forcée | Set controller in Bypass state (RC_ControllerStateSetBypass)
Source de contrôle ventilateur
|  |  | Source de contrôle ventilateur | Fan speed setting (RC_FanSelect)
Sortie chauffage
|  |  | Mode | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Sortie chauffage (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Mode | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Sortie chauffage | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Sortie chauffage 2
|  |  | Mode | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Sortie chauffage 2 (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Mode | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Sortie chauffage 2 | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Sortie refroidissement
|  |  | Mode | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Sortie refroidissement (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Mode | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Sortie refroidissement | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Sortie refroidissement 2
|  |  | Mode | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Sortie refroidissement 2 (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Mode | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Sortie refroidissement 2 | Room control Cool2 output digital (RC_RoomCool2OutputDO)
Sortie VAV
|  |  | Mode | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | Sortie VAV (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
Sortie VAV 2
|  |  | Mode | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | Sortie VAV 2 (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Sortie change-over
|  |  | Mode | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Sortie change-over (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Sortie VAV change-over
|  |  | Mode | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Sortie VAV change-over (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Sortie vanne 6 voies
|  |  | Mode | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Mode | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Valeur réglée (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Sortie vanne 6 voies (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Sortie zone supplémentaire
|  |  | Mode | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Sortie zone supplémentaire | Extra Zone output analog (RC_ExtraZoneOutputAO)
Commande du ventilateur EC
|  |  | Mode | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Valeur réglée (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | Commande du ventilateur EC (%) | Current EC fan speed (RC_ECFanSpeed)
Sortie contrôle CO2
|  |  | Mode | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Valeur réglée (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | Sortie contrôle CO2 (%) | CO2 control analog out (RC_CO2ControlAO)
Sortie contrôle d’humidification
|  |  | Mode | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Sortie contrôle d’humidification (%) | Humidify analog out (RC_HumidifyOutputAO)
Sortie contrôle de déshumidification
|  |  | Mode | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Valeur réglée (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Sortie contrôle de déshumidification (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
Sortie contrôle COV
|  |  | Mode | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Valeur réglée (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | Sortie contrôle COV (%) | VOC control analog out (RC_VOCControlAO)
Sortie zone supplémentaire active
|  |  | Mode | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Sortie zone supplémentaire active | Extra Zone active (RC_ExtraZoneActive)
Sortie ventilation forcée
|  |  | Mode | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Sortie ventilation forcée | Forced ventilation output (RC_ForcedVentDO)
Contrôle des sorties physiques
UO1
|  |  | UO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1 : | Value set for output (IoDo_1_value)
|  |  | Mode | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Valeur réglée | Override value (IoDo_1_override)
UO2
|  |  | UO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO1 : | Value set for output (IoDo_2_value)
|  |  | Mode | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Valeur réglée | Override value (IoDo_2_override)
AO1
|  |  | UO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1 : (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Valeur réglée | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Valeur réglée | Override value (IoAnaIn_2_override)
Étalonnage de la sonde CO2
|  |  | Activer autocalibrage automatique | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Cible CO2 ppm autocalibrage automatique (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Exécuter un réétalonnage forcé de la sonde CO2 | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Niveau de CO2 de référence pour le réétalonnage forcé (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Dernier résultat de réétalonnage forcé (-9999 = Erreur) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Régler la sonde de CO2 sur les paramètres d'usine par défaut | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Sortie relais
|  |  | État du relais | Value set for output (IoDo_3_value)
|  |  | Mode | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Valeur réglée | Override value (IoDo_3_override)
Capteur PIR
|  |  | Capteur PIR | Filtered value from sensor (IoDiIn_4_value)
|  |  | Mode | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Valeur réglée | Override value (IoDiIn_4_override)
Appareil
Identification du régulateur
Identification du régulateur
|  |  | Nom | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Emplacement | Controller location (ControllerLocation)
|  |  | Projet | (ControllerProject)
Communication
Réglages du port
|  |  | Fonction Port 1 | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Vitesse de transmission Port 1 | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Parité Port 1 | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Adresse Modbus | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | Adresse BACnet MSTP | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | Adresse maître MSTP max. | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | ID bas BACnet | BACnet device ID (BACnetDeviceID)
|  |  | Nom d’objet de l’appareil BACnet | BACnet device object name (BACnetDeviceObjectName)
|  |  | Mot de passe | BACnet password (BACnetPassword)
Bluetooth
|  |  | Fonction Bluetooth | Function for BLE button (BleButtonMode)
|  |  | Arrêter après (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Défaut de communication
|  |  | Action en cas d’échec | Offline function (RC_OfflineFunction)
|  |  | Délai Expiré (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | État de secours | State to set during communication faults (RC_ControllerStateFail)
|  |  | État | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Redémarrer régulateur | Write to this register will trigger resets with different reset reasons (product_reset)

## nl
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overzicht
Systeem
|  |  | Regelaar | Model number (Model)
|  |  | Versie | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus adres | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP adres | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet apparaat ID | BACnet device ID (BACnetDeviceID)
|  |  | Verzamel alarm | Sum Alarm (RC_SumAlarm)
Ruimte
|  |  | Regelaar status | Current state (RC_ControllerState)
|  |  | Modus | Current controller mode (RC_ControllerMode)
|  |  | Ruimte temperatuur (°C) | Room temperature (RC_RoomTemp)
|  |  | Inblaas temperatuur (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Ruimte gewenst (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Gewenste verstelling (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC ventilator snelheid (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 niveau (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Ruimte vochtigheid (%) | Relative humidity (RC_Humidity)
|  |  | VOC-index | VOC index (RC_VOC)
|  |  | Aanwezigheid detector | Presence indication (RC_Presence)
|  |  | Condensatie | Condensation indication (RC_DICondensation)
Extra zone
|  |  | Extra zone temperatuur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zone gewenst (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extra zone actief uitgang | Extra Zone active (RC_ExtraZoneActive)
Huidige waarden
Ruimte regelaar volgorde
|  |  | Volgorde 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Volgorde 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Volgorde 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Huidige waarden
|  |  | Modus | Current controller mode (RC_ControllerMode)
|  |  | Ruimte temperatuur (°C) | Room temperature (RC_RoomTemp)
|  |  | Ruimte gewenst (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Gewenste verstelling (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Verwarmvraag (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Koelvraag (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Verwarming uitgang (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Verwarming 2 uitgang (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Koeling uitgang (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Koeling 2 uitgang (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV uitgang (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 uitgang (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperatuur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over status | Change-over status (RC_ChangeOverState)
|  |  | Change-over uitgang (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV temperatuur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV status | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV uitgang (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-wegklep uitgang (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 niveau (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 gewenst (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Relais uitgang
|  |  | Relais status | Value set for output (IoDo_3_value)
|  |  | Bron 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Grenswaarde deactiveren | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Grenswaarde activeren | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Bron 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Grenswaarde deactiveren | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Grenswaarde activeren | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Bron 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Grenswaarde deactiveren | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Grenswaarde activeren | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Bron 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Grenswaarde deactiveren | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Grenswaarde activeren | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timer status | Current timer state (rt_exttime_state)
|  |  | Actieve timerwaarde | Time remaining (rt_exttime_timeleft)
Ingangen/Uitgangen
Universele ingangen
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universele uitgangen
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoge uitgangen
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne sensoren
|  |  | Ruimte temperatuur (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 sensor (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RV sensor (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
Alarmen
Alarmen
|  |  | Verzamel alarm | Sum Alarm (RC_SumAlarm)
|  |  | Defecte opnemer | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hoge ruimte temperatuur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Lage ruimte temperatuur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hoog CO2-gehalte | High CO2 alarm (RC_AlarmCO2High)
|  |  | Extern alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Uitgang in handbediening | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Foutcode temperatuuropnemer | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Foutcode vochtigheidsopnemer | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Foutcode VOC sensor | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Foutcode CO2 sensor | Detailed fault description (IoAnaIn_8_errorFlags)
Info
Regelaar-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Naam | (ControllerName)
|  |  | Omschrijving | Controller description (ControllerDescription)
|  |  | Locatie | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Configuratie
Regel functies
Ruimte regelaar volgorde
|  |  | Volgorde 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Volgorde 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Volgorde 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Verwarming
|  |  | Max. limiet (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min. limiet (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Uitschakelvertraging ventilator voor elektrische verwarming | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Volg change-over status | Heat1 included in change-over function (RC_Heat1InChangeOver)
Verwarming 2
|  |  | Max. limiet (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min. limiet (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Uitschakelvertraging ventilator voor elektrische verwarming | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Volg change-over status | Heat2 included in change-over function (RC_Heat2InChangeOver)
Koeling
|  |  | Max. limiet (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min. limiet (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Volg change-over status | Cool1 included in change-over function (RC_Cool1InChangeOver)
Koeling 2
|  |  | Max. limiet (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min. limiet (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Volg change-over status | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max. limiet (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min. limiet, uit (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min. limiet, afwezig (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min. limiet, stand-by (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min. limiet, aanwezig (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max. limiet bij verwarmen (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Volg change-over status | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Max. limiet (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min. limiet, uit (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min. limiet, afwezig (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min. limiet, stand-by (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min. limiet, aanwezig (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max. limiet bij verwarmen (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Volg change-over status | VAV2 included in change-over function (RC_VAV2InChangeOver)
VAV-regelingen
|  |  | Koelvraag | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 niveau | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Vochtigheid | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max. limiet (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min. limiet (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Modus | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperatuur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Verwarming hysterese (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Koel hysterese (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Vertragingstijd klep (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Max. limiet (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min. limiet, uit (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min. limiet, afwezig (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min. limiet, stand-by (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min. limiet, aanwezig (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Modus | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperatuur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Verwarming hysterese (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Koel hysterese (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Vertragingstijd klep (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-weg klep
|  |  | Volg 1 volledig open (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Volg 1 start openen (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Volg 2 volledig open (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Volg 2 start openen (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Centraal punt (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Centraal punt hysterese (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Volgorde | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Volg change-over status | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Regelaar status
|  |  | Ingeschakelde regelaar status | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Uitgeschakelde regelaar status | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Raam open | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tijd in geforceerde ventilatiemodus (min) | Bypass time (minutes) (RC_BypassTime)
Geforceerde ventilatie
|  |  | Actief wanneer | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start limiet (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Aanwezigheid detector
|  |  | Actuele status | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Vertraging actief (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Vertraging inactief (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 activering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 niveau (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysterese (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Gebruik interne PIR voor aanwezigheid | Use internal PID sensor for presence detection (RC_PIDPresence)
Extra zone
Extra zone
|  |  | Extra zone functie | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Uitschakelen als status lager dan | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Uitschakelen als hoofdzonemodus afwijkt van functie | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min. limiet (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max. limiet (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Ingangen/Uitgangen
Universele ingangen
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universele uitgangen
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | U01 periode thermische klep (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | U01 regelsignaal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | U02 periode thermische klep (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | U02 regelsignaal | Unit converter (IoAnaOut_2_unit)
Analoge uitgangen
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 regelsignaal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 regelsignaal | Unit converter (IoAnaOut_4_unit)
Ventilator regeling
Ventilator regeling
|  |  | Ruimte regelaar | Select fan control mode (RC_FanControlMode)
|  |  | CO2 niveau | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Vochtigheid | Fan is controlled by humidity output (RC_FanControlHumidity)
EC Ventilator regeling
|  |  | Snelheid bij geen vraag | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Uit onder de vraag (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese voor ventilator snelheid verlagen (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start snelheid (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. snelheid in automodus (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Snelheid geforceerde ventilatie | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Snelheid geforceerde ventilatie (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Snelheid 1 uitgang (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Snelheid 2 uitgang (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Snelheid 3 uitgang (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Vorm beveiliging | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Kick-start ventilator
|  |  | Kick-start tijd (s) | Fan kick start time (RC_FanKickStartTime)
Vertraging ventilator uit
|  |  | Uit vertraging tijd (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimum snelheid | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilatorboost
|  |  | Modus | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost tijd (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display en menu's
Display
|  |  | Start scherm | What to display during device startup (DisplayStartupMode)
|  |  | Display weergave | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Schakelen tussen temperatuur en CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Display weergave bij waarde wijziging | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | CO2-waarde afronden | Min step for CO2 value (RC_CO2Step)
|  |  | Helderheid hoog (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Tijdsduur hoog, 0 = Altijd aan (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Helderheid laag (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Tijdsduur laag, 0 = Nooit uit (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Weer te geven waarden
Timer
|  |  | Display modus | How to show the timer in the display (rt_exttime_mode)
|  |  | Animatie | Show animation in timer view (rt_exttime_animate)
|  |  | Led inschakelen wanneer actief | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Stapgrootte in minuten (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Aantal stappen | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Huidige timerwaarde (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timer status | Current timer state (rt_exttime_state)
Aangepaste teksten
|  |  | Display weergave | When to show the custom text (rt_text_visability)
|  |  | Display modus | Single or dual row text in display (rt_text_mode)
|  |  | Scroll modus | Scroll mode (rt_text_display_scroll_mode)
|  |  | Lettertype | What font to use for the display text (rt_text_font)
|  |  | Scroll vertraging (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Aangepaste tekst timerwaarde (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Aangepaste tekst rij 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Aangepaste tekst rij 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Aangepaste tekst 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Aangepaste tekst 2 | String to show on row 2 in the display (rt_text_row_2)
Led-indicatie
|  |  | Helderheid (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 led-indicatie | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gele led CO2-niveau (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rode led CO2-niveau (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menu
|  |  | Gewenste waarde aanpassen | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Menu pagina modus | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu pagina | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator menu pagina | Enable Fan menu page (App_EnableMenuFan)
|  |  | Geforceerde ventilatie menu pagina | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Geforceerde ventilatie overwerktimer | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Vochtigheid menu pagina | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu pagina | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu pagina | Enable VOC menu page (App_EnableMenuVOC)
Modus menu-opties
|  |  | Menu titel tekst | Mode menu title (App_ModeMenuTitle)
|  |  | Modus Uit inschakelen | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Modus Afwezig inschakelen | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Modus Stand-by inschakelen | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Modus Aanwezig inschakelen | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Modus Geforceerde ventilatie inschakelen | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Modus Uit tekst | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Modus Afwezig tekst | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Modus Stand-by tekst | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Modus Aanwezig tekst | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Modus Geforceerde ventilatie tekst | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Modus Auto tekst | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menu-opties
|  |  | Menu titel tekst | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Status Verwarming inschakelen | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Status Koeling inschakelen | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Status Auto inschakelen | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Status Verwarming tekst | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Status Koeling tekst | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Status Auto tekst | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Servomotoren
Aan/uit-uitgangen
|  |  | Verwarmingshysterese, ruimte temperatuur (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Koelhysterese, ruimte temperatuur (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, extra zone temperatuur (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Kleppentest
|  |  | Kleppentest | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Interval verwarmen (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Interval verwarmen 2 (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Interval koelen (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Interval koelen 2 (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Interval change-over (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Interval 6-wegklep (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Duur verwarming (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Duur verwarming 2 (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Duur koeling (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Duur koeling 2 (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Duur change-over (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | Duur 6-wegklep (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoge ingangen
Temperatuur ingang
|  |  | Filtertijd (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatuur ingang 0-10V
|  |  | Waarde bij 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Waarde bij 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 ingang
|  |  | Waarde bij 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Waarde bij 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtertijd (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Vochtigheid ingang
|  |  | Waarde bij 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Waarde bij 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtertijd (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow ingang
|  |  | Waarde bij 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Waarde bij 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtertijd (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC ingang
|  |  | Waarde bij 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Waarde bij 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtertijd (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Gewenste waarden
Ruimte gewenst
|  |  | Verwarming, aanwezig (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Koeling, aanwezig (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Verwarming, stand-by (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Koeling, stand-by (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Verwarming, afwezig (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Koeling, afwezig (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Vorst beveiliging (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Gewenste verstelling
|  |  | Max gewenste verstelling omhoog (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max gewenste verstelling omlaag (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Gewenste verstelling (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zone
|  |  | Extra zone gewenst (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 gewenst (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Vochtigheid
|  |  | Vochtigheid gewenst (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC gewenst | Setpoint for VOC control (RC_VOCSetpoint)
PI-regelaars
Ruimte
|  |  | P-band (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-tijd (s) | I-time for room PID controller (RC_RoomPIDItime)
Inblaas regeling
|  |  | Regeling actief | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Versterkingsfactor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. verwarmingstemperatuur (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. verwarmingstemperatuur (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. koeltemperatuur (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. koeltemperatuur (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Vorst beveiliging temperatuur (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zone
|  |  | P-band (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-tijd (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-tijd (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Vochtigheid
|  |  | P-band (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-tijd (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-tijd (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm instellingen
Alarm ruimte temperatuur
|  |  | Bovengrenswaarde (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Ondergrenswaarde (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Alarm CO2-niveau
|  |  | Bovengrenswaarde (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Invoer aanpassingen
UI1
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_1_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_1_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_1_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_1_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_2_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_2_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_2_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_2_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_2_offset)
Ruimte temperatuur
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_5_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_5_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_5_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_5_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_5_offset)
Ruimte vochtigheid
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_6_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_6_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_6_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_6_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_6_offset)
VOC sensor
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_7_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_7_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_7_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_7_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_7_offset)
CO2 sensor
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Minimumwaarde | Scale for input (IoAnaIn_8_min_in)
|  |  | Maximumwaarde | Scale for input (IoAnaIn_8_max_in)
|  |  | Aangepaste minimumwaarde | Scale for input (IoAnaIn_8_min_out)
|  |  | Aangepaste maximumwaarde | Scale for input (IoAnaIn_8_max_out)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_8_offset)
Uitgang instellingen
UO1
|  |  | Minimumwaarde | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimumwaarde | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimumwaarde | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimumwaarde | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Handmatig/Auto
Externe waarden
Ruimte temperatuur
|  |  | Hand sturing | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Gewenst (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Ruimte temperatuur (°C) | Room temperature (RC_RoomTemp)
Inblaas temperatuur
|  |  | Hand sturing | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Gewenst (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Inblaas temperatuur (°C) | Supply air temperature (RC_SupplyAirTemp)
Extra zone temperatuur
|  |  | Hand sturing | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Gewenst (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zone temperatuur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperatuur
|  |  | Hand sturing | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Gewenst (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperatuur (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV temperatuur
|  |  | Hand sturing | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Gewenst (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV temperatuur (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 niveau
|  |  | Hand sturing | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Gewenst (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 niveau (ppm) | Room CO2 level (RC_CO2Level)
Ruimte vochtigheid
|  |  | Hand sturing | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Gewenst (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Ruimte vochtigheid (%) | Relative humidity (RC_Humidity)
Lucht Flow
|  |  | Hand sturing | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Gewenst | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Lucht Flow | Air flow (RC_AirFlow)
VOC-index
|  |  | Hand sturing | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Gewenst | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-index | VOC index (RC_VOC)
Aanwezigheid detector
|  |  | Hand sturing | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Gewenst | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Aanwezigheid detector | Presence indication (RC_Presence)
Open raam
|  |  | Hand sturing | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Gewenst | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Open raam | Open window indication (RC_DIOpenWindow)
Condensatie
|  |  | Hand sturing | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Gewenst | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensatie | Condensation indication (RC_DICondensation)
Extern alarm (DI)
|  |  | Hand sturing | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Gewenst | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Extern alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Hand sturing | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Gewenst | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Hand sturing | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Gewenst | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Handmatig/Auto
Regelaar status
|  |  | Regelaar status | Current state (RC_ControllerState)
|  |  | GBS overschrijven | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Uitschakelen | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Geforceerde ventilatie | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator regeling
|  |  | Ventilator regeling | Fan speed setting (RC_FanSelect)
Verwarming uitgang
|  |  | Modus | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Verwarming uitgang (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Modus | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Verwarming uitgang | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Verwarming 2 uitgang
|  |  | Modus | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Verwarming 2 uitgang (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Modus | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Verwarming 2 uitgang | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Koeling uitgang
|  |  | Modus | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Koeling uitgang (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Modus | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Koeling uitgang | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Koeling 2 uitgang
|  |  | Modus | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Koeling 2 uitgang (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Modus | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Koeling 2 uitgang | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV uitgang
|  |  | Modus | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV uitgang (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 uitgang
|  |  | Modus | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 uitgang (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over uitgang
|  |  | Modus | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over uitgang (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV uitgang
|  |  | Modus | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Gewenst (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV uitgang (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-wegklep uitgang
|  |  | Modus | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Modus | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Gewenst (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-wegklep uitgang (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extra zone uitgang
|  |  | Modus | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Gewenst (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extra zone uitgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC Ventilator regeling
|  |  | Modus | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Gewenst (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC Ventilator regeling (%) | Current EC fan speed (RC_ECFanSpeed)
CO2-regeling uitgang
|  |  | Modus | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Gewenst (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2-regeling uitgang (%) | CO2 control analog out (RC_CO2ControlAO)
Vochtigheidsregeling uitgang
|  |  | Modus | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Gewenst (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Vochtigheidsregeling uitgang (%) | Humidify analog out (RC_HumidifyOutputAO)
Ontvochtigingsregeling uitgang
|  |  | Modus | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Gewenst (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Ontvochtigingsregeling uitgang (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC-regeling uitgang
|  |  | Modus | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Gewenst (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC-regeling uitgang (%) | VOC control analog out (RC_VOCControlAO)
Extra zone actief uitgang
|  |  | Modus | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extra zone actief uitgang | Extra Zone active (RC_ExtraZoneActive)
Geforceerde ventilatie uitgang
|  |  | Modus | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Geforceerde ventilatie uitgang | Forced ventilation output (RC_ForcedVentDO)
Hardware regeling
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Modus | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Gewenst | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Modus | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Gewenst | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Gewenst | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Gewenst | Override value (IoAnaIn_2_override)
Kalibratie CO2-sensor
|  |  | Automatische zelfkalibratie inschakelen | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatische zelfkalibratie doel CO2 ppm (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Voer geforceerde herkalibratie van CO2-sensor uit | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Referentie CO2-niveau voor geforceerde herkalibratie (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Laatste geforceerde herkalibratieresultaat (-9999 = fout) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | CO2-sensor instellen op fabrieksinstellingen | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relais uitgang
|  |  | Relais status | Value set for output (IoDo_3_value)
|  |  | Modus | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Gewenst | Override value (IoDo_3_override)
PIR sensor
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Modus | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Gewenst | Override value (IoDiIn_4_override)
Apparaat
Regelaar-ID
Regelaar-ID
|  |  | Naam | (ControllerName)
|  |  | Omschrijving | Controller description (ControllerDescription)
|  |  | Locatie | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Communicatie
Poortinstellingen
|  |  | Poort 1 functie | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Poort 1 baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Poort 1 pariteit | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus adres | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP adres | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP max master adres | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet apparaat ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet apparaat objectnaam | BACnet device object name (BACnetDeviceObjectName)
|  |  | Wachtwoord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-functie | Function for BLE button (BleButtonMode)
|  |  | Uitschakeling na (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Communicatiestoring
|  |  | Foutactie | Offline function (RC_OfflineFunction)
|  |  | Time-out (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback status | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Herstart regelaar | Write to this register will trigger resets with different reset reasons (product_reset)

## sv
RCX-2.0-1-02 ꟷ Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Översikt
System
|  |  | Regulator | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbusadress | Active Modbus unit ID (ModbusUnitID)
|  |  | MSTP-adress för BACnet | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet enhets-ID | BACnet device ID (BACnetDeviceID)
|  |  | Summerlarm | Sum Alarm (RC_SumAlarm)
Rum
|  |  | Regulatorläge | Current state (RC_ControllerState)
|  |  | Driftläge | Current controller mode (RC_ControllerMode)
|  |  | Rumstemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Tilluftstemperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Rumsbörvärde (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Börvärdesjustering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC-fläkthastighet (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2-nivå (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Luftfuktighet i rum (%) | Relative humidity (RC_Humidity)
|  |  | VOC-index | VOC index (RC_VOC)
|  |  | Närvarostyrning | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Extra zon
|  |  | Extra zon, temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zon, börvärde (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Aktiv utgång för extra zon | Extra Zone active (RC_ExtraZoneActive)
Ärvärden
Rumsstyrningssekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Ärvärden
|  |  | Driftläge | Current controller mode (RC_ControllerMode)
|  |  | Rumstemperatur (°C) | Room temperature (RC_RoomTemp)
|  |  | Rumsbörvärde (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Börvärdesjustering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Värmebehov (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Kylbehov (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Värme-utgång (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Värme 2-utgång (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Kyla-utgång (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Kyla 2-utgång (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV-utgång (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2-utgång (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over-temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over-läge | Change-over status (RC_ChangeOverState)
|  |  | Change-over-utgång (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV-temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV-läge | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | VAV-utgång för change-over (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Utgång för 6-vägsventil (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2-nivå (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2-börvärde (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Reläutgång
|  |  | Relästatus | Value set for output (IoDo_3_value)
|  |  | Källa 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Inaktivera gräns | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Aktivera gräns | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Källa 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Inaktivera gräns | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Aktivera gräns | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Källa 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Inaktivera gräns | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Aktivera gräns | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Källa 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Inaktivera gräns | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Aktivera gräns | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timerstatus | Current timer state (rt_exttime_state)
|  |  | Aktivt timervärde | Time remaining (rt_exttime_timeleft)
Ingångar/Utgångar
Universella ingångar
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universella utgångar
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoga utgångar
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interna givare
|  |  | Rumstemperatur (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2-givare (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Fuktgivare (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC-givare | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR-givare | Filtered value from sensor (IoDiIn_4_value)
Larm
Larm
|  |  | Summerlarm | Sum Alarm (RC_SumAlarm)
|  |  | Givarfel | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hög rumstemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Låg rumstemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hög CO2-nivå | High CO2 alarm (RC_AlarmCO2High)
|  |  | Externt larm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Utgång i manuellt läge | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Felkod för temperaturgivare | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Felkod för fuktighetsgivare | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Felkod för VOC-givare | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Felkod för CO2-givare | Detailed fault description (IoAnaIn_8_errorFlags)
Om
Regulator-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Namn | (ControllerName)
|  |  | Beskrivning | Controller description (ControllerDescription)
|  |  | Plats | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Konfigurering
Reglerfunktioner
Rumsstyrningssekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Värme
|  |  | Max.gräns (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min.gräns (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Fläkt av, fördröjning för elvärme | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Följ change-over-läge | Heat1 included in change-over function (RC_Heat1InChangeOver)
Värme 2
|  |  | Max.gräns (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min.gräns (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Fläkt av, fördröjning för elvärme | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Följ change-over-läge | Heat2 included in change-over function (RC_Heat2InChangeOver)
Kyla
|  |  | Max.gräns (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min.gräns (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Ställ in på max. vid forcerad ventilation | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Följ change-over-läge | Cool1 included in change-over function (RC_Cool1InChangeOver)
Kyla 2
|  |  | Max.gräns (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min.gräns (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Ställ in på max. vid forcerad ventilation | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Följ change-over-läge | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max.gräns (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min.gräns, av (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min.gräns, unoccupied (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min.gräns, standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min.gräns, Närvaro (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Maxgräns vid värme (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Följ change-over-läge | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Max.gräns (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min.gräns, av (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min.gräns, unoccupied (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min.gräns, standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min.gräns, Närvaro (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Maxgräns vid värme (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Följ change-over-läge | VAV2 included in change-over function (RC_VAV2InChangeOver)
VAV-reglering källa
|  |  | Kylbehov | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2-nivå | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Luftfuktighet | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max.gräns (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min.gräns (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Driftläge | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over-temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Värmehysteres (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Kylhysteres (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Ventil, fördröjningstid (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over-VAV
|  |  | Max.gräns (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min.gräns, av (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min.gräns, unoccupied (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min.gräns, standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min.gräns, Närvaro (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Driftläge | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over-temperatur (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Värmehysteres (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Kylhysteres (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Ventil, fördröjningstid (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-vägsventil
|  |  | Sekv. 1 helt öppen (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Sekv. 1 börja öppna (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Sekv. 2 helt öppen (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Sekv. 2 börja öppna (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Mittpunkt (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Hysteres för mittpunkt (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sekvensordning | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Följ change-over-läge | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Regulatorläge
|  |  | Förinställt läge | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Shutdown-läge | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Öppet fönster-läge | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tid i forcerat ventilationsläge (min) | Bypass time (minutes) (RC_BypassTime)
Forcerad ventilation
|  |  | Aktiv när | Forced ventilation function (RC_ForcedVentMode)
|  |  | Startgräns (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Närvarostyrning
|  |  | Närvaroläge | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Aktiv fördröjning (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inaktiv fördröjning (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2-aktivering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2-nivå (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2-hysteres (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Använd intern PIR för närvaro | Use internal PID sensor for presence detection (RC_PIDPresence)
Extra zon
Extra zon
|  |  | Funktion för extra zon | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Inaktiverad under läge | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Inaktivera om huvudzonläge skiljer sig från funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min.gräns (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max.gräns (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Ingångar/Utgångar
Universella ingångar
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universella utgångar
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 tidsperiod för termisk ventil (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 styrsignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 tidsperiod för termoventil (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 styrsignal | Unit converter (IoAnaOut_2_unit)
Analoga utgångar
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 styrsignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 styrsignal | Unit converter (IoAnaOut_4_unit)
Fläktstyrning
Fläktregleringskälla
|  |  | Rumsregulator | Select fan control mode (RC_FanControlMode)
|  |  | CO2-nivå | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Luftfuktighet | Fan is controlled by humidity output (RC_FanControlHumidity)
EC-fläktreglering
|  |  | Hastighet vid inget behov | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Av vid under behov (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysteres för minskning av fläkthastigheten (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Starthastighet (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. hastighet i autoläge (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Hastighet för forcerad ventilation | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Hastighet för forcerad ventilation (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Hastighet 1 utgång (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Hastighet 2 utgång (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Hastighet 3 utgång (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Mögelskydd | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Fläkt, kickstart
|  |  | Tid för kick-start (s) | Fan kick start time (RC_FanKickStartTime)
Fläkt, frånslagsfördröjning
|  |  | Av-tidsfördröjning (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Min. hastighet | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Fläkt, boost
|  |  | Driftläge | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Tid för boostning (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display och menyer
Display
|  |  | Startskärm | What to display during device startup (DisplayStartupMode)
|  |  | Visningsläge | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Alternerande temp/CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Börvärdesläge | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Avrunda CO2-värdet till närmaste | Min step for CO2 value (RC_CO2Step)
|  |  | Full ljusstyrka (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dim timeout, 0 = Alltid full (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Dimmad ljusstyrka (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Av-timeout, 0 = Aldrig av (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Värden att visa
Timer
|  |  | Displayläge | How to show the timer in the display (rt_exttime_mode)
|  |  | Animering | Show animation in timer view (rt_exttime_animate)
|  |  | Tänd LED när aktiv | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Minuter per steg (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Antal steg | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Aktuellt timervärde (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timerstatus | Current timer state (rt_exttime_state)
Anpassade texter
|  |  | Visningsläge | When to show the custom text (rt_text_visability)
|  |  | Displayläge | Single or dual row text in display (rt_text_mode)
|  |  | Bläddringsläge | Scroll mode (rt_text_display_scroll_mode)
|  |  | Teckensnitt | What font to use for the display text (rt_text_font)
|  |  | Bläddring, fördröjning (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Timervärde för anpassad text (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Anpassad text rad 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Anpassad text rad 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Anpassad text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Anpassad text 2 | String to show on row 2 in the display (rt_text_row_2)
LED-indikering
|  |  | Ljusstyrka (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED-indikering | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gul LED CO2-nivå (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Röd LED CO2-nivå (ppm) | CO2 level for red led (RC_CO2LevelRed)
Meny
|  |  | Börvärdesjustering | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Menysida driftläge | Enable Mode menu page (App_EnableMenuMode)
|  |  | Menysida för change-over | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Menysida för fläkt | Enable Fan menu page (App_EnableMenuFan)
|  |  | Menysida för forcerad ventilation | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Förlängd drift för forcerad ventilation | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Menysida för luftfuktighet | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | Menysida för CO2 | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | Menysida för VOC | Enable VOC menu page (App_EnableMenuVOC)
Alternativ i driftslägesmenyn
|  |  | Text för menyrubrik | Mode menu title (App_ModeMenuTitle)
|  |  | Aktivera driftläget Av | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Aktivera driftläget Ej Närvaro | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Aktivera driftläget Standby | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Aktivera driftläget Närvaro | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Aktivera driftläget Forcerad ventilation | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Text för driftläget Av | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Text för driftläget Ej Närvaro | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Text för driftläget Standby | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Text för driftläget Närvaro | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Text för driftläget Forcerad ventilation | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Text för driftläget Auto | Mode menu Auto state text (App_ModeMenuAutoText)
Alternativ i change-over-menyn
|  |  | Text för menyrubrik | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Aktivera driftläget Värme | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Aktivera läget Kyla | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Aktivera läget Auto | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Text för läget Värme | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Text för läget Kyla | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Text för läget Auto | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Ställdon
Till/Från-utgångar
|  |  | Värmehysteres, rumstemperatur (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Kylhysteres, rumstemperatur (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysteres, temperatur extra zon (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Ventilmotionering
|  |  | Ventilmotionering | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Intervall för värme (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Intervall för värme 2 (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Intervall för kyla (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Intervall för kyla 2 (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Intervall för change-over (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Intervall för 6-vägsventil (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Värme, varaktighet (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Värme 2, varaktighet (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Kyla, varaktighet (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Kyla 2, varaktighet (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over, varaktighet (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-vägsventil, varaktighet (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoga ingångar
Temperaturingång
|  |  | Filtertid (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperaturingång 0–10 V
|  |  | Värde vid 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Värde vid 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2-ingång
|  |  | Värde vid 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Värde vid 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtertid (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Luftfuktighet ingång
|  |  | Värde vid 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Värde vid 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtertid (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flödesingång
|  |  | Värde vid 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Värde vid 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtertid (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC-ingång
|  |  | Värde vid 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Värde vid 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtertid (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Börvärden
Rumsbörvärden
|  |  | Värme, occupied (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Kyla, occupied (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Värme, standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Kyla, standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Värme, unoccupied (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Kyla, unoccupied (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frostskydd (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Börvärdesjustering
|  |  | Max. justering uppåt (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max. justering nedåt (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Börvärdesjustering (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zon
|  |  | Extra zon, börvärde (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2-börvärde (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Luftfuktighet
|  |  | Fuktighetsbörvärde (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC-börvärde | Setpoint for VOC control (RC_VOCSetpoint)
Regulatorinställningar
Rum
|  |  | P-band (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-tid (s) | I-time for room PID controller (RC_RoomPIDItime)
Kaskadreglering
|  |  | Reglering aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskadfaktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. temperatur värme (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. temperatur värme (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. temperatur kyla (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. temperatur kyla (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frostskyddstemperatur (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zon
|  |  | P-band (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-tid (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-tid (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Luftfuktighet
|  |  | P-band (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-tid (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-tid (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Larminställningar
Larm rumstemperatur
|  |  | Högt gränsvärde (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Lågt gränsvärde (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Larm CO2-nivå
|  |  | Högt gränsvärde (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Ingångsjusteringar
UI1
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_1_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_1_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_1_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_1_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_2_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_2_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_2_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_2_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_2_offset)
Rumstemperatur
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_5_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_5_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_5_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_5_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_5_offset)
Luftfuktighet i rum
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_6_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_6_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_6_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_6_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_6_offset)
VOC-givare
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_7_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_7_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_7_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_7_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_7_offset)
CO2-givare
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Minimivärde | Scale for input (IoAnaIn_8_min_in)
|  |  | Maxvärde | Scale for input (IoAnaIn_8_max_in)
|  |  | Justerat minimivärde | Scale for input (IoAnaIn_8_min_out)
|  |  | Justerat maxvärde | Scale for input (IoAnaIn_8_max_out)
|  |  | Offsetjustering | Offset for input (IoAnaIn_8_offset)
Utgångsjusteringar
UO1
|  |  | Minimivärde | Scale for output (IoAnaOut_1_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimivärde | Scale for output (IoAnaOut_2_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimivärde | Scale for output (IoAnaOut_3_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimivärde | Scale for output (IoAnaOut_4_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Manuell/Auto
Fjärringångsvärden
Rumstemperatur
|  |  | Fjärrinställning | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Inställt värde (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Rumstemperatur (°C) | Room temperature (RC_RoomTemp)
Tilluftstemperatur
|  |  | Fjärrinställning | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Inställt värde (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Tilluftstemperatur (°C) | Supply air temperature (RC_SupplyAirTemp)
Extra zon, temperatur
|  |  | Fjärrinställning | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Inställt värde (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zon, temperatur (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over-temperatur
|  |  | Fjärrinställning | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Inställt värde (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over-temperatur (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV-temperatur
|  |  | Fjärrinställning | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Inställt värde (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV-temperatur (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2-nivå
|  |  | Fjärrinställning | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Inställt värde (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2-nivå (ppm) | Room CO2 level (RC_CO2Level)
Luftfuktighet i rum
|  |  | Fjärrinställning | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Inställt värde (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Luftfuktighet i rum (%) | Relative humidity (RC_Humidity)
Luftflöde
|  |  | Fjärrinställning | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Inställt värde | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Luftflöde | Air flow (RC_AirFlow)
VOC-index
|  |  | Fjärrinställning | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Inställt värde | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-index | VOC index (RC_VOC)
Närvarostyrning
|  |  | Fjärrinställning | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Inställt värde | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Närvarostyrning | Presence indication (RC_Presence)
Öppet fönster
|  |  | Fjärrinställning | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Inställt värde | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Öppet fönster | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Fjärrinställning | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Inställt värde | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Externt larm (DI)
|  |  | Fjärrinställning | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Inställt värde | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Externt larm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Fjärrinställning | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Inställt värde | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Fjärrinställning | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Inställt värde | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuell/Auto
Regulatorläge
|  |  | Regulatorläge | Current state (RC_ControllerState)
|  |  | Fjärrlägesinställning | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Shutdown | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Forcerad ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Fläktregleringskälla
|  |  | Fläktregleringskälla | Fan speed setting (RC_FanSelect)
Värme-utgång
|  |  | Driftläge | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Värme-utgång (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Driftläge | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Värme-utgång | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Värme 2-utgång
|  |  | Driftläge | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Värme 2-utgång (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Driftläge | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Värme 2-utgång | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Kyla-utgång
|  |  | Driftläge | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Kyla-utgång (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Driftläge | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Kyla-utgång | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Kyla 2-utgång
|  |  | Driftläge | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Kyla 2-utgång (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Driftläge | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Kyla 2-utgång | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV-utgång
|  |  | Driftläge | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV-utgång (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2-utgång
|  |  | Driftläge | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2-utgång (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over-utgång
|  |  | Driftläge | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over-utgång (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
VAV-utgång för change-over
|  |  | Driftläge | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Inställt värde (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | VAV-utgång för change-over (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Utgång för 6-vägsventil
|  |  | Driftläge | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Driftläge | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Inställt värde (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Utgång för 6-vägsventil (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Utgång för extra zon
|  |  | Driftläge | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Inställt värde (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Utgång för extra zon | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC-fläktreglering
|  |  | Driftläge | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Inställt värde (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC-fläktreglering (%) | Current EC fan speed (RC_ECFanSpeed)
Utgång för CO2-reglering
|  |  | Driftläge | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Inställt värde (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | Utgång för CO2-reglering (%) | CO2 control analog out (RC_CO2ControlAO)
Utgång för fuktreglering
|  |  | Driftläge | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Inställt värde (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Utgång för fuktreglering (%) | Humidify analog out (RC_HumidifyOutputAO)
Utgång för avfuktningsreglering
|  |  | Driftläge | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Inställt värde (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Utgång för avfuktningsreglering (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
Utgång för VOC-reglering
|  |  | Driftläge | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Inställt värde (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | Utgång för VOC-reglering (%) | VOC control analog out (RC_VOCControlAO)
Aktiv utgång för extra zon
|  |  | Driftläge | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Aktiv utgång för extra zon | Extra Zone active (RC_ExtraZoneActive)
Utgång för forcerad ventilation
|  |  | Driftläge | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Utgång för forcerad ventilation | Forced ventilation output (RC_ForcedVentDO)
Hårdvarustyrning
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Inställt värde | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Inställt värde | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Inställt värde | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Inställt värde | Override value (IoAnaIn_2_override)
Kalibrering av CO2-givare
|  |  | Aktivera automatisk självkalibrering | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Baseline för automatisk självkalibrering CO2 ppm (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Kör forcerad Omkalibrering av CO2-givare | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Referens-nivå för CO2 vid forcerad Omkalibrering (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Senaste forcerade omkalibreringsresultat (-9999 = Fel) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Återställ CO2-givare till fabriksinställningar | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Reläutgång
|  |  | Relästatus | Value set for output (IoDo_3_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Inställt värde | Override value (IoDo_3_override)
PIR-givare
|  |  | PIR-givare | Filtered value from sensor (IoDiIn_4_value)
|  |  | Driftläge | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Inställt värde | Override value (IoDiIn_4_override)
Enhet
Regulator-ID
Regulator-ID
|  |  | Namn | (ControllerName)
|  |  | Beskrivning | Controller description (ControllerDescription)
|  |  | Plats | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Portinställningar
|  |  | Port 1 funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Baudhastighet, port 1 | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Paritet, port 1 | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbusadress | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | MSTP-adress för BACnet | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | Högsta master-adress för MSTP | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet enhets-ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet-enhetens objektnamn | BACnet device object name (BACnetDeviceObjectName)
|  |  | Lösenord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-funktion | Function for BLE button (BleButtonMode)
|  |  | Stäng av efter (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Kommunikationsfel
|  |  | Felhantering | Offline function (RC_OfflineFunction)
|  |  | Avbrott (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Reservläge | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Återställ
Återställ
|  |  | Starta om regulator | Write to this register will trigger resets with different reset reasons (product_reset)