## Variables
Regio Ardo/Eedo 2.1-1-00 - Variable list | [14 empty] | Revision: | A
|  |  | Available | EXOline |  |  | Modbus |  |  |  |  | BACnet
Name | Default | Description | only in | Type | Load | Cell | Register type | Register | Address | Scale | Offset | Object type | Instance | Unit | Writeable | Variable type
RegioSoftware |  | Type of Regio software (0=RPC) |  | X | 2 | 0 | InputRegister | 300002 | 1 | 1 |  | analog_value | 40003 | no_units
RegioVerMajor | 2 | Major Version |  | X | 2 | 1 | InputRegister | 300003 | 2 | 1 |  | analog_value | 40004 | no_units
RegioVerMinor | 1 | Minor Version |  | X | 2 | 2 | InputRegister | 300004 | 3 | 1 |  | analog_value | 40005 | no_units
RegioVerBranch | 1 | Branch Version (0=Beta, 1=Official) |  | X | 2 | 3 | InputRegister | 300005 | 4 | 1 |  | analog_value | 40006 | no_units
RegioRevision |  | Revision |  | X | 2 | 4 | InputRegister | 300006 | 5 | 1 |  | analog_value | 40007 | no_units
RegioRoomTempExt |  | Room temp external sensor |  | R | 2 | 66 | InputRegister | 300007 | 6 | 10 |  | analog_value | 40008 | degrees_celsius
RegioAIChangeOverTemp |  | Change over |  | R | 2 | 69 | InputRegister | 300008 | 7 | 10 |  | analog_value | 40009 | degrees_celsius
RegioOutdoorTemp |  | Outdoor temp |  | R | 2 | 72 | InputRegister | 300009 | 8 | 10 |  | analog_value | 40010 | degrees_celsius
RegioCondensation |  | Condense |  | R | 2 | 75 | InputRegister | 300010 | 9 | 1 |  | analog_value | 40011 | no_units
RegioRoomCO2 |  | Room CO2 |  | R | 2 | 78 | InputRegister | 300011 | 10 | 1 |  | analog_value | 40012 | parts_per_million
RegioRoomRH |  | Room RH |  | R | 2 | 81 | InputRegister | 300012 | 11 | 1 |  | analog_value | 40013 | percent_relative_humidity
RegioSupplyAirTemp |  | Supply air temperature |  | R | 2 | 84 | InputRegister | 300013 | 12 | 10 |  | analog_value | 40014 | degrees_celsius
RegioUnderfloorTemp |  | Underfloor Temperature |  | R | 2 | 87 | InputRegister | 300110 | 109 | 10 |  | analog_value | 40111 | degrees_celsius
RegioFlow |  | Flow value |  | R | 2 | 90 | InputRegister | 300112 | 111 | 10 |  | analog_value | 40027 | no_units
RegioRoomTempExtZone2 |  | Room temp external sensor Room2 | Ardo | R | 2 | 132 | InputRegister | 300039 | 38 | 10 |  | analog_value | 40040 | degrees_celsius
RegioOutDoorTempZone2 |  | Outdoor temp Room2 | Ardo | R | 2 | 138 | InputRegister | 300040 | 39 | 10 |  | analog_value | 40041 | degrees_celsius
RegioCondensationZone2 |  | Condense Room2 | Ardo | R | 2 | 141 | InputRegister | 300041 | 40 | 1 |  | analog_value | 40042 | no_units
RegioRoomCO2Zone2 |  | Room CO2 Room2 | Ardo | R | 2 | 144 | InputRegister | 300042 | 41 | 1 |  | analog_value | 40043 | parts_per_million
RegioRoomRHZone2 |  | Room RH Room2 | Ardo | R | 2 | 147 | InputRegister | 300043 | 42 | 1 |  | analog_value | 40044 | degrees_celsius
RegioSupplyAirTempZone2 |  | Supply air temperature Room2 | Ardo | R | 2 | 150 | InputRegister | 300044 | 43 | 10 |  | analog_value | 40045 | degrees_celsius
RegioUnderfloorTempZone2 |  | Underfloor Temperature Room 2 | Ardo | R | 2 | 153 | InputRegister | 300111 | 110 | 10 |  | analog_value | 40112 | degrees_celsius
RegioFlowZone2 |  | Air flow value, Room 2 | Ardo | R | 2 | 156 | InputRegister | 300113 | 112 | 10 |  | analog_value | 40028 | no_units
RegioOpenWindowInd |  | Open window indication |  | L | 2 | 229 | DiscreteInput | 100002 | 1 |  |  | binary_value | 20001
RegioCondensationAlarm |  | Alarm Condensation indication |  | L | 2 | 230 | DiscreteInput | 100003 | 2 |  |  | binary_value | 20002
RegioPresenceInd |  | Presence indication |  | L | 2 | 231 | DiscreteInput | 100004 | 3 |  |  | binary_value | 20003
RegioChangeOverInd |  | Change over indication |  | L | 2 | 232 | DiscreteInput | 100005 | 4 |  |  | binary_value | 20004
RegioOpenWindowIndZone2 |  | Open window indication Room2 | Ardo | L | 2 | 248 | DiscreteInput | 100047 | 46 |  |  | binary_value | 20046
RegioCondensationAlarmZone2 |  | Alarm Condensation indication Room2 | Ardo | L | 2 | 249 | DiscreteInput | 100048 | 47 |  |  | binary_value | 20047
RegioPresenceIndZone2 |  | Presence indication Room2 | Ardo | L | 2 | 250 | DiscreteInput | 100049 | 48 |  |  | binary_value | 20048
RegioAnaOut1 |  | Analog output 1 |  | R | 2 | 270 | InputRegister | 300014 | 13 | 1 |  | analog_value | 40015 | volts
RegioAnaOut2 |  | Analog output 2 |  | R | 2 | 273 | InputRegister | 300015 | 14 | 1 |  | analog_value | 40016 | volts
RegioAnaOut3 |  | Analog output 1 |  | R | 2 | 276 | InputRegister | 300016 | 15 | 1 |  | analog_value | 40017 | volts
RegioAnaOut4 |  | Analog output 2 |  | R | 2 | 279 | InputRegister | 300017 | 16 | 1 |  | analog_value | 40018 | volts
RegioHeatSeq1 |  | Control valve Heating 1 |  | R | 2 | 297 | InputRegister | 300018 | 17 | 1 |  | analog_value | 40019 | percent
RegioHeatSeq2 |  | Control valve Heating 2 |  | R | 2 | 300 | InputRegister | 300019 | 18 | 1 |  | analog_value | 40020 | percent
RegioCoolSeq1 |  | Control valve Cooling 1 |  | R | 2 | 303 | InputRegister | 300020 | 19 | 1 |  | analog_value | 40021 | percent
RegioCoolSeq2 |  | Not used |  | R | 2 | 306 | InputRegister | 300021 | 20 | 1 |  | analog_value | 40022 | percent
RegioHeatCoolOutput |  | Control valve Heating/Cooling |  | R | 2 | 309 | InputRegister | 300022 | 21 | 1 |  | analog_value | 40023 | percent
RegioVAVOutput |  | Control VAV damper |  | R | 2 | 312 | InputRegister | 300023 | 22 | 1 |  | analog_value | 40024 | percent
RegioECFanOutput |  | Control EC Fan |  | R | 2 | 315 | InputRegister | 300024 | 23 | 1 |  | analog_value | 40025 | percent
RegioHeatSeq1Zone2 |  | Control valve Heating 1 Room2 | Ardo | R | 2 | 363 | InputRegister | 300045 | 44 | 1 |  | analog_value | 40046 | percent
RegioHeatSeq2Zone2 |  | Control valve Heating 2 Room2 | Ardo | R | 2 | 366 | InputRegister | 300046 | 45 | 1 |  | analog_value | 40047 | percent
RegioCoolSeq1Zone2 |  | Control valve Cooling 1 Room2 | Ardo | R | 2 | 369 | InputRegister | 300047 | 46 | 1 |  | analog_value | 40048 | percent
RegioCoolSeq2Zone2 |  | Not used | Ardo | R | 2 | 372 | InputRegister | 300048 | 47 | 1 |  | analog_value | 40049 | percent
RegioHeatCoolOutputZone2 |  | Control valve Heating/Cooling Room2 | Ardo | R | 2 | 375 | InputRegister | 300049 | 48 | 1 |  | analog_value | 40050 | percent
RegioVAVOutputZone2 |  | Control VAV damper Room2 | Ardo | R | 2 | 378 | InputRegister | 300050 | 49 | 1 |  | analog_value | 40051 | percent
RegioECFanOutputZone2 |  | Control EC Fan Room2 | Ardo | R | 2 | 381 | InputRegister | 300051 | 50 | 1 |  | analog_value | 40052 | percent
RegioDigOut1 |  | Digital output 1 |  | L | 2 | 430 | DiscreteInput | 100006 | 5 |  |  | binary_value | 20005
RegioDigOut2 |  | Digital output 2 |  | L | 2 | 431 | DiscreteInput | 100007 | 6 |  |  | binary_value | 20006
RegioDigOut3 |  | Digital output 3 |  | L | 2 | 432 | DiscreteInput | 100008 | 7 |  |  | binary_value | 20007
RegioDigOut4 |  | Digital output 4 |  | L | 2 | 433 | DiscreteInput | 100009 | 8 |  |  | binary_value | 20008
RegioDigOut5 |  | Digital output 5 |  | L | 2 | 434 | DiscreteInput | 100010 | 9 |  |  | binary_value | 20009
RegioDigOut6 |  | Digital output 6 |  | L | 2 | 435 | DiscreteInput | 100011 | 10 |  |  | binary_value | 20010
RegioFanSpeed1Output |  | Start Fan Speed 1 |  | L | 2 | 443 | DiscreteInput | 100012 | 11 |  |  | binary_value | 20011
RegioFanSpeed2Output |  | Start Fan Speed 2 |  | L | 2 | 444 | DiscreteInput | 100013 | 12 |  |  | binary_value | 20012
RegioFanSpeed3Output |  | Start Fan Speed 3 |  | L | 2 | 445 | DiscreteInput | 100014 | 13 |  |  | binary_value | 20013
RegioLightingOutput |  | Start signal Lighting |  | L | 2 | 446 | DiscreteInput | 100015 | 14 |  |  | binary_value | 20014
RegioSunBlindsInOutput |  | In signal Blind |  | L | 2 | 447 | DiscreteInput | 100016 | 15 |  |  | binary_value | 20015
RegioSunBlindsOutOutput |  | Out signal Blind |  | L | 2 | 448 | DiscreteInput | 100017 | 16 |  |  | binary_value | 20016
RegioForcedVentOutput |  | Start forced ventilation |  | L | 2 | 449 | DiscreteInput | 100018 | 17 |  |  | binary_value | 20017
RegioHeat1IncOutput |  | Increase heat 1 valve |  | L | 2 | 450 | DiscreteInput | 100019 | 18 |  |  | binary_value | 20018
RegioHeat1DecOutput |  | Decrease heat 1 valve |  | L | 2 | 451 | DiscreteInput | 100020 | 19 |  |  | binary_value | 20019
RegioHeat1PulsPropOutput |  | Thermal heat 1 valve |  | L | 2 | 452 | DiscreteInput | 100021 | 20 |  |  | binary_value | 20020
RegioHeat2IncOutput |  | Increase heat 2 valve |  | L | 2 | 453 | DiscreteInput | 100022 | 21 |  |  | binary_value | 20021
RegioHeat2DecOutput |  | Decrease heat 2 valve |  | L | 2 | 454 | DiscreteInput | 100023 | 22 |  |  | binary_value | 20022
RegioHeat2PulsPropOutput |  | Thermal heat 2 valve |  | L | 2 | 455 | DiscreteInput | 100024 | 23 |  |  | binary_value | 20023
RegioCool1IncOutput |  | Increase cool 1 valve |  | L | 2 | 456 | DiscreteInput | 100025 | 24 |  |  | binary_value | 20024
RegioCool1DecOutput |  | Decrease cool 1 valve |  | L | 2 | 457 | DiscreteInput | 100026 | 25 |  |  | binary_value | 20025
RegioCool1PulsPropOutput |  | Thermal cool 1 valve |  | L | 2 | 458 | DiscreteInput | 100027 | 26 |  |  | binary_value | 20026
RegioCool2IncOutput |  | Not used |  | L | 2 | 459 | DiscreteInput | 100028 | 27 |  |  | binary_value | 20027
RegioCool2DecOutput |  | Not used |  | L | 2 | 460 | DiscreteInput | 100029 | 28 |  |  | binary_value | 20028
RegioCool2PulsPropOutput |  | Not used |  | L | 2 | 461 | DiscreteInput | 100030 | 29 |  |  | binary_value | 20029
RegioHeatCoolIncOutput |  | Increase Heat cool valve |  | L | 2 | 462 | DiscreteInput | 100031 | 30 |  |  | binary_value | 20030
RegioHeatCoolDecOutput |  | Decrease Heat cool valve |  | L | 2 | 463 | DiscreteInput | 100032 | 31 |  |  | binary_value | 20031
RegioHeatCoolPulsPropOutput |  | Thermal Heat cool valve |  | L | 2 | 464 | DiscreteInput | 100033 | 32 |  |  | binary_value | 20032
RegioSumAlarm |  | Sum alarm |  | L | 2 | 465 | DiscreteInput | 100034 | 33 |  |  | binary_value | 20033
RegioSumAlarmA |  | Sum alarm A |  | L | 2 | 466 | DiscreteInput | 100035 | 34 |  |  | binary_value | 20034
RegioSumAlarmB |  | Sum alarm B |  | L | 2 | 467 | DiscreteInput | 100036 | 35 |  |  | binary_value | 20035
RegioFanSpeed1OutputZone2 |  | Start Fan Speed 1 Room2 | Ardo | L | 2 | 483 | DiscreteInput | 100050 | 49 |  |  | binary_value | 20049
RegioFanSpeed2OutputZone2 |  | Start Fan Speed 2 Room2 | Ardo | L | 2 | 484 | DiscreteInput | 100051 | 50 |  |  | binary_value | 20050
RegioFanSpeed3OutputZone2 |  | Start Fan Speed 3 Room2 | Ardo | L | 2 | 485 | DiscreteInput | 100052 | 51 |  |  | binary_value | 20051
RegioLightingOutputZone2 |  | Start signal Lighting Room2 | Ardo | L | 2 | 486 | DiscreteInput | 100053 | 52 |  |  | binary_value | 20052
RegioSunBlindsInOutputZone2 |  | In signal Blind Room2 | Ardo | L | 2 | 487 | DiscreteInput | 100054 | 53 |  |  | binary_value | 20053
RegioSunBlindsOutOutputZone2 |  | Out signal Blind Room2 | Ardo | L | 2 | 488 | DiscreteInput | 100055 | 54 |  |  | binary_value | 20054
RegioForcedVentOutputZone2 |  | Start forced ventilation Room2 | Ardo | L | 2 | 489 | DiscreteInput | 100056 | 55 |  |  | binary_value | 20055
RegioHeat1IncOutputZone2 |  | Increase heat 1 valve Room2 | Ardo | L | 2 | 490 | DiscreteInput | 100057 | 56 |  |  | binary_value | 20056
RegioHeat1DecOutputZone2 |  | Decrease heat 1 valve Room2 | Ardo | L | 2 | 491 | DiscreteInput | 100058 | 57 |  |  | binary_value | 20057
RegioHeat1PulsPropOutputZone2 |  | Thermal heat 1 valve Room2 | Ardo | L | 2 | 492 | DiscreteInput | 100059 | 58 |  |  | binary_value | 20058
RegioHeat2IncOutputZone2 |  | Increase heat 2 valve Room2 | Ardo | L | 2 | 493 | DiscreteInput | 100060 | 59 |  |  | binary_value | 20059
RegioHeat2DecOutputZone2 |  | Decrease heat 2 valve Room2 | Ardo | L | 2 | 494 | DiscreteInput | 100061 | 60 |  |  | binary_value | 20060
RegioHeat2PulsPropOutputZone2 |  | Thermal heat 2 valve Room2 | Ardo | L | 2 | 495 | DiscreteInput | 100062 | 61 |  |  | binary_value | 20061
RegioCool1IncOutputZone2 |  | Increase cool 1 valve Room2 | Ardo | L | 2 | 496 | DiscreteInput | 100063 | 62 |  |  | binary_value | 20062
RegioCool1DecOutputZone2 |  | Decrease cool 1 valve Room2 | Ardo | L | 2 | 497 | DiscreteInput | 100064 | 63 |  |  | binary_value | 20063
RegioCool1PulsPropOutputZone2 |  | Thermal cool 1 valve Room2 | Ardo | L | 2 | 498 | DiscreteInput | 100065 | 64 |  |  | binary_value | 20064
RegioCool2IncOutputZone2 |  | Not used | Ardo | L | 2 | 499 | DiscreteInput | 100066 | 65 |  |  | binary_value | 20065
RegioCool2DecOutputZone2 |  | Not used | Ardo | L | 2 | 500 | DiscreteInput | 100067 | 66 |  |  | binary_value | 20066
RegioCool2PulsPropOutputZone2 |  | Not used | Ardo | L | 2 | 501 | DiscreteInput | 100068 | 67 |  |  | binary_value | 20067
RegioHeatCoolIncOutputZone2 |  | Increase Heat cool valve Room2 | Ardo | L | 2 | 502 | DiscreteInput | 100069 | 68 |  |  | binary_value | 20068
RegioHeatCoolDecOutputZone2 |  | Decrease Heat cool valve Room2 | Ardo | L | 2 | 503 | DiscreteInput | 100070 | 69 |  |  | binary_value | 20069
RegioHeatCoolPulsPropOutputZone2 |  | Thermal Heat cool valve Room2 | Ardo | L | 2 | 504 | DiscreteInput | 100071 | 70 |  |  | binary_value | 20070
RegioSumAlarmZone2 |  | Sum alarm Room2 | Ardo | L | 2 | 505 | DiscreteInput | 100072 | 71 |  |  | binary_value | 20071
RegioSumAlarmAZone2 |  | Sum alarm A Room2 | Ardo | L | 2 | 506 | DiscreteInput | 100073 | 72 |  |  | binary_value | 20072
RegioSumAlarmBZone2 |  | Sum alarm B Room2 | Ardo | L | 2 | 507 | DiscreteInput | 100074 | 73 |  |  | binary_value | 20073
RegioRoomTemp |  | Room temperature internal or external |  | R | 2 | 547 | InputRegister | 300025 | 24 | 10 |  | analog_value | 40026 | no_units
RegioRoomTempZone2 |  | Room temperature internal or external Room2 | Ardo | R | 2 | 550 | InputRegister | 300052 | 51 | 10 |  | analog_value | 40053 | degrees_celsius
RegioRoomTempAverage |  | Average room temperature internal or external |  | R | 2 | 553 | InputRegister | 300066 | 65 | 10 |  | analog_value | 40067 | degrees_celsius
RegioAIChangeOverAverage |  | Average Change over Temperature |  | R | 2 | 556 | InputRegister | 300067 | 66 | 10 |  | analog_value | 40068 | degrees_celsius
RegioOutDoorTempAverage |  | Average Temperature from all controllers |  | R | 2 | 559 | InputRegister | 300068 | 67 | 10 |  | analog_value | 40069 | degrees_celsius
RegioCondenseAverage |  | Condense Average |  | R | 2 | 562 | InputRegister | 300069 | 68 | 1 |  | analog_value | 40070 | no_units
RegioRoomCO2Average |  | Average CO2 from all controllers |  | R | 2 | 565 | InputRegister | 300070 | 69 | 1 |  | analog_value | 40071 | parts_per_million
RegioRoomRHAverage |  | Average Humidity from all controllers |  | R | 2 | 568 | InputRegister | 300071 | 70 | 1 |  | analog_value | 40072 | percent_relative_humidity
RegioSupplyAirTempAverage |  | SupplyAir Temperature from all controllers |  | R | 2 | 571 | InputRegister | 300072 | 71 | 10 |  | analog_value | 40073 | degrees_celsius
RegioDIOpenWindowCombined |  | Open window indication all Controllers |  | L | 2 | 574 | DiscreteInput | 100096 | 95 |  |  | binary_value | 20095
RegioDICondenseAlarmCombined |  | Alarm condensation indication all Controllers |  | L | 2 | 575 | DiscreteInput | 100097 | 96 |  |  | binary_value | 20096
RegioDIPresenceCombined |  | Presence indication all Controllers (This is the combination of all pins not actually the presence state) |  | L | 2 | 576 | DiscreteInput | 100098 | 97 |  |  | binary_value | 20097
RegioDIChangeoverCombined |  | Change over indication all Controllers |  | L | 2 | 577 | DiscreteInput | 100099 | 98 |  |  | binary_value | 20098
RegioSetpointOffsetCombined |  | Setpoint offset , last changed offset from all controllers |  | R | 2 | 578 | InputRegister | 300073 | 72 | 10 |  | analog_value | 40074 | degrees_celsius
RegioPIDSetP |  | Setpoint Sent to PID |  | R | 2 | 584 | InputRegister | 300028 | 27 | 10 |  | analog_value | 40029 | degrees_celsius
RegioSetPAdjustment |  | Setpoint Adjustment |  | R | 2 | 594 | InputRegister | 300029 | 28 | 10 |  | analog_value | 40030 | degrees_celsius
RegioPIDSetPZone2 |  | Setpoint Sent to PID Room2 | Ardo | R | 2 | 600 | InputRegister | 300056 | 55 | 10 |  | analog_value | 40057 | degrees_celsius
RegioPIDAlaManualZone2 |  | Alarm Output: The Regulator is in Manual mode Room2 | Ardo | L | 2 | 603 | DiscreteInput | 100075 | 74 |  |  | binary_value | 20074
RegioPIDOutputZone2 |  | Controller output Room2 | Ardo | R | 2 | 604 | InputRegister | 300053 | 52 | 1 |  | analog_value | 40054 | no_units
RegioSetPAdjustmentZone2 |  | Setpoint Adjustment for Room2 | Ardo | R | 2 | 610 | InputRegister | 300057 | 56 | 10 |  | analog_value | 40058 | degrees_celsius
RegioControlState | 3 | Current unit state 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 4=Bypass |  | X | 2 | 613 | InputRegister | 300026 | 25 | 1 |  | multi_state_value 1=Off 2=Unoccupied 3=Stand-by 4=Occupied 5=ByPass | 40027
RegioRoomTempControlState |  | Current controller state 0=Heating 1=Cooling |  | L | 2 | 614 | DiscreteInput | 100037 | 36 |  |  | binary_value | 20036
RegioHeatCoolSymbol |  | Current controller state 0=Off 1=Heating 2=Cooling 3=Heating and Cooling |  | X | 2 | 615 | InputRegister | 300027 | 26 | 1 |  | multi_state_value 1=Heating 2=Cooling 3=Nothing | 40028
RegioHeatOutput |  | Control signal Heating 0-100 % |  | R | 2 | 616 | InputRegister | 300030 | 29 | 1 |  | analog_value | 40031 | percent
RegioCoolOutput |  | Control signal Cooling 0-100 % |  | R | 2 | 619 | InputRegister | 300031 | 30 | 1 |  | analog_value | 40032 | percent
RegioVAVOutputSignal |  | Control signal VAV 0-100% |  | R | 2 | 622 | InputRegister | 300032 | 31 | 1 |  | analog_value | 40033 | percent
RegioECFanOutputSignal |  | Control signal EC fan 0-100% |  | R | 2 | 625 | InputRegister | 300033 | 32 | 1 |  | analog_value | 40034 | percent
RegioFanSpeed |  | Current 3speed fan speed 0=Off 1=Speed1 2=Speed2 3=Speed3 |  | X | 2 | 628 | InputRegister | 300034 | 33 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 | 40035
RegioECFanSpeedIndex |  | Current EC fan speed converted to index, used in RU 0=Off 1=Speed1 2=Speed2 3=Speed3 |  | X | 2 | 629 | InputRegister | 300035 | 34 | 1 |  | analog_value | 40036 | no_units
RegioFanSpeedSelectCombined | 4 | Fan speed Selected 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Forced ventilation 5=Auto |  | X | 2 | 630 | InputRegister | 300036 | 35 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 5=Auto | 40037
RegioSunBlindsState |  | Blind Position 0=In 1=Out |  | L | 2 | 631 | DiscreteInput | 100038 | 37 |  |  | binary_value | 20037
RegioPresence |  | Presence indication |  | L | 2 | 632 | DiscreteInput | 100039 | 38 |  |  | binary_value | 20038
RegioCO2Presence |  | Is set if presence if CO2 is high |  | L | 2 | 633 | DiscreteInput | 100040 | 39 |  |  | binary_value | 20039
RegioByPassRunMin |  | Time left in Bypass mode (min) |  | I | 2 | 634 | InputRegister | 300037 | 36 | 1 |  | analog_value | 40038 | minutes
RegioAIChangeOverState |  | Is set if change over from analog input |  | L | 2 | 636 | DiscreteInput | 100041 | 40 |  |  | binary_value | 20040
RegioChangeOverState |  | Is set if change over |  | L | 2 | 637 | DiscreteInput | 100042 | 41 |  |  | binary_value | 20041
RegioRoomTempSensorAlarm |  | Is set if sensor alarm on room sensor (Internal or external) |  | L | 2 | 638 | DiscreteInput | 100043 | 42 |  |  | binary_value | 20042
RegioTimeGroupOcc |  | Time Group 'Occupied' (No. 1). |  | L | 2 | 639 | DiscreteInput | 100044 | 43 |  |  | binary_value | 20043
RegioTimeGroupUnOcc |  | Time Group 'UnOccupied' (No. 2). |  | L | 2 | 640 | DiscreteInput | 100045 | 44 |  |  | binary_value | 20044
RegioTimeGroupLighting |  | Time Group 'Lighting' (No. 3). |  | L | 2 | 641 | DiscreteInput | 100046 | 45 |  |  | binary_value | 20045
RegioMasterSlaveState |  | Current State in Removable Walls Feature 0=StandAlone 1=Master 2=Slave 3=Slave with comm error running as standalone |  | X | 2 | 642 | InputRegister | 300038 | 37 | 1 |  | multi_state_value 1=StandAlone 2=Master 3=Slave 4=Slave with comm error running as standalone | 40039
RegioControlStateZone2 | 3 | Current unit state Room2 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 4=Bypass | Ardo | X | 2 | 643 | InputRegister | 300054 | 53 | 1 |  | multi_state_value 1=Off 2=Unoccupied 3=Stand-by 4=Occupied 5=ByPass | 40055
RegioRoomTempControlStateZone2 |  | Current controller state Room2 0=Heating 1=Cooling | Ardo | L | 2 | 644 | DiscreteInput | 100076 | 75 |  |  | binary_value | 20075
RegioHeatCoolSymbolZone2 |  | Current controller state Room2 0=Off, 1=Heating 2=Cooling 3=Heating and Cooling | Ardo | X | 2 | 645 | InputRegister | 300055 | 54 | 1 |  | multi_state_value 1=Heating 2=Cooling 3=Nothing | 40056
RegioHeatOutputZone2 |  | Control signal Heating 0-100 % Room2 | Ardo | R | 2 | 646 | InputRegister | 300058 | 57 | 1 |  | analog_value | 40059 | percent
RegioCoolOutputZone2 |  | Control signal Cooling 0-100 % Room2 | Ardo | R | 2 | 649 | InputRegister | 300059 | 58 | 1 |  | analog_value | 40060 | percent
RegioVAVOutputSignalZone2 |  | Control signal VAV 0-100% Room2 | Ardo | R | 2 | 652 | InputRegister | 300060 | 59 | 1 |  | analog_value | 40061 | percent
RegioECFanOutputSignalZone2 |  | Control signal EC fan 0-100% Room2 | Ardo | R | 2 | 655 | InputRegister | 300061 | 60 | 1 |  | analog_value | 40062 | percent
RegioFanSpeedZone2 |  | Current 3speed fan speed Room2 0=Off 1=Speed1 2=Speed2 3=Speed3 | Ardo | X | 2 | 658 | InputRegister | 300062 | 61 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 | 40063
RegioECFanSpeedIndexZone2 |  | Current EC fan speed converted to index, used in RU Room2 0=Off 1=Speed1 2=Speed2 3=Speed3 | Ardo | X | 2 | 659 | InputRegister | 300063 | 62 | 1 |  | analog_value | 40064 | no_units
RegioFanSpeedSelectCombinedZone2 | 4 | Fan speed Selected Room2 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Forced ventilation 5=Auto | Ardo | X | 2 | 660 | InputRegister | 300064 | 63 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 5=Auto | 40065
RegioSunBlindsStateZone2 |  | Blind Position Room2 0=In 1=Out | Ardo | L | 2 | 661 | DiscreteInput | 100077 | 76 |  |  | binary_value | 20076
RegioPresenceZone2 |  | Presence indication Room2 | Ardo | L | 2 | 662 | DiscreteInput | 100078 | 77 |  |  | binary_value | 20077
RegioCO2PresenceZone2 |  | Is set if presence if CO2 is high Room2 | Ardo | L | 2 | 663 | DiscreteInput | 100079 | 78 |  |  | binary_value | 20078
RegioByPassRunMinZone2 |  | Time left in Bypass mode (min) Room2 | Ardo | I | 2 | 664 | InputRegister | 300065 | 64 | 1 |  | analog_value | 40066 | no_units
RegioAIChangeOverStateZone2 |  | Is set if change over from analog input Room2 | Ardo | L | 2 | 666 | DiscreteInput | 100080 | 79 |  |  | binary_value | 20079
RegioChangeOverStateZone2 |  | Is set if change over Room2 | Ardo | L | 2 | 667 | DiscreteInput | 100081 | 80 |  |  | binary_value | 20080
RegioRoomTempSensorAlarmZone2 |  | Is set if sensor alarm on room sensor (Internal or external) Room2 | Ardo | L | 2 | 668 | DiscreteInput | 100082 | 81 |  |  | binary_value | 20081
RegioTimeGroupOccZone2 |  | Time Group 'Occupied' (No. 1). Room2 | Ardo | L | 2 | 669 | DiscreteInput | 100083 | 82 |  |  | binary_value | 20082
RegioTimeGroupUnOccZone2 |  | Time Group 'UnOccupied' (No. 2). Room2 | Ardo | L | 2 | 670 | DiscreteInput | 100084 | 83 |  |  | binary_value | 20083
RegioTimeGroupLightingZone2 |  | Time Group 'Lighting' (No. 3). Room2 | Ardo | L | 2 | 671 | DiscreteInput | 100085 | 84 |  |  | binary_value | 20084
RegioExerciseOnHeat1 |  | Valve Heat 1 in exercise |  | L | 2 | 672 | DiscreteInput | 100086 | 85 |  |  | binary_value | 20085
RegioExerciseOnHeat2 |  | Valve Heat 2 in exercise |  | L | 2 | 673 | DiscreteInput | 100087 | 86 |  |  | binary_value | 20086
RegioExerciseOnCool1 |  | Valve Cool 1 in exercise |  | L | 2 | 674 | DiscreteInput | 100088 | 87 |  |  | binary_value | 20087
RegioExerciseOnCool2 |  | Not used |  | L | 2 | 675 | DiscreteInput | 100089 | 88 |  |  | binary_value | 20088
RegioExerciseOnHeatCool |  | Valve HeatCool in exercise |  | L | 2 | 676 | DiscreteInput | 100090 | 89 |  |  | binary_value | 20089
RegioExerciseOnHeat1Zone2 |  | Valve Heat 1 in exercise Room2 | Ardo | L | 2 | 677 | DiscreteInput | 100091 | 90 |  |  | binary_value | 20090
RegioExerciseOnHeat2Zone2 |  | Valve Heat 2 in exercise Room2 | Ardo | L | 2 | 678 | DiscreteInput | 100092 | 91 |  |  | binary_value | 20091
RegioExerciseOnCool1Zone2 |  | Valve Cool 1 in exercise Room2 | Ardo | L | 2 | 679 | DiscreteInput | 100093 | 92 |  |  | binary_value | 20092
RegioExerciseOnCool2Zone2 |  | Not used | Ardo | L | 2 | 680 | DiscreteInput | 100094 | 93 |  |  | binary_value | 20093
RegioExerciseOnHeatCoolZone2 |  | Valve HeatCool in exercise Room2 | Ardo | L | 2 | 681 | DiscreteInput | 100095 | 94 |  |  | binary_value | 20094
RegioCommFailsafe |  | Communication Failsafe variable, needs to be set to 1 by the Master to indicate communication |  | L | 2 | 774 | Coil | 94 | 93 |  |  | binary_value | 10009 |  | X
RegioCommFailsafeActive |  | Indicates communication failsafe state |  | L | 2 | 775 | DiscreteInput | 100100 | 99 |  |  | binary_value | 20099
RegioAnaIn1Aux |  | Analog Input 1 value, when configured as Ext. Analog Input |  | R | 2 | 780 | InputRegister | 300106 | 105 | 10 |  | analog_value | 40107 | no_units
RegioAnaIn2Aux |  | Analog Input 2 value, when configured as Ext. Analog Input |  | R | 2 | 783 | InputRegister | 300107 | 106 | 10 |  | analog_value | 40108 | no_units
RegioAnaIn3Aux |  | Analog Input 3 value, when configured as Ext. Analog Input |  | R | 2 | 786 | InputRegister | 300108 | 107 | 10 |  | analog_value | 40109 | no_units
RegioAnaIn4Aux |  | Analog Input 4 value, when configured as Ext. Analog Input | Ardo | R | 2 | 789 | InputRegister | 300109 | 108 | 10 |  | analog_value | 40110 | no_units
RegioDigIn1Aux |  | Digital Input 1 value when configured as Ext. Digital Input |  | L | 2 | 799 | DiscreteInput | 100101 | 100 |  |  | binary_value | 20100
RegioDigIn2Aux |  | Digital Input 2 value when configured as Ext. Digital Input |  | L | 2 | 800 | DiscreteInput | 100102 | 101 |  |  | binary_value | 20101
RegioDigIn3Aux |  | Digital Input 3 value when configured as Ext. Digital Input |  | L | 2 | 801 | DiscreteInput | 100103 | 102 |  |  | binary_value | 20102
RegioDigIn4Aux |  | Digital Input 4 value when configured as Ext. Digital Input | Ardo | L | 2 | 802 | DiscreteInput | 100104 | 103 |  |  | binary_value | 20103
RegioInput1RU1 |  |  |  | I | 2 | 898 | InputRegister | 300115 | 114
RegioInput2RU1 |  |  |  | I | 2 | 900 | InputRegister | 300116 | 115
RegioInput3RU1 |  |  |  | I | 2 | 902 | InputRegister | 300117 | 116
RegioInput1RU2 |  |  | Ardo | I | 2 | 910 | InputRegister | 300118 | 117
RegioInput2RU2 |  |  | Ardo | I | 2 | 912 | InputRegister | 300119 | 118
RegioInput3RU2 |  |  | Ardo | I | 2 | 914 | InputRegister | 300120 | 119
RegioAi1 |  | Configuration for Analog Input 1 0=Disable 1=External room temp 2=ChangeOver temp 3=Outdoor temp 4=Condensation 5=CO2 sensor 6=RH sensor 11=Supply air Temp 12=Extra zone temperature, room 22 13 External room temp 0-10 V 3 14=Flow sensor 3 101=External room temp room 2 103=Outdoor temp room 2 104=Condensation room 2 105=CO2 sensor room 2 106=RH sensor room 2 111=Supply air temp room 2 112=Extra zone temperature, room 2 2 113=External room temp 0-10 V room 2 3 114=Flow sensor room 2 3 200=Ext. Analog Input PT1000 2 201=Ext. Analog Input 0…10 V 2 |  | X | 3 | 1 | HoldingRegister | 400144 | 143 | 1
RegioAi2 |  | Configuration for Analog Input 2 |  | X | 3 | 2 | HoldingRegister | 400145 | 144 | 1
RegioAi3 |  | Configuration for Analog Input 3 |  | X | 3 | 3 | HoldingRegister | 400146 | 145 | 1
RegioAi4 |  | Configuration for Analog Input 4 | Ardo | X | 3 | 4 | HoldingRegister | 400147 | 146 | 1
RegioDi1 | 3 | Configuration for Digital Input 1 0=Disable 1=Open window 2=Not Used 3=Presence detector 4=Changeover 101=Open window room 2 102=Not used 103=Presence detector room 2 |  | X | 3 | 10 | HoldingRegister | 400148 | 147 | 1
RegioDi2 | 1 | Configuration for Digital Input 2 |  | X | 3 | 11 | HoldingRegister | 400149 | 148 | 1
RegioDi3 |  | Configuration for Digital Input 3 |  | X | 3 | 12 | HoldingRegister | 400150 | 149 | 1
RegioDi4 |  | Configuration for Digital Input 4 | Ardo | X | 3 | 13 | HoldingRegister | 400151 | 150 | 1
RegioCI | 1 | Configuration for Digital Condensation Input 1 0=Disable 1=Regin's KG-A/1 sensor 2=Regin's KG-A/1 sensor room 2 |  | X | 3 | 22 | HoldingRegister | 400154 | 153 | 1
RegioCI2 |  | Configuration for Digital Condensation Input 2 | Ardo | X | 3 | 23 | HoldingRegister | 400155 | 154 | 1
RegioAo1 | 1 | Configuration for Analog Output 1 0=Disable 1=Heat 2=Heat 2 3=Cool 4=Not used 5=Changeover / 6-way Valve 6=VAV 7=EC fan 101=Heat room 2 102=Heat 2 room 2 103=Cool room 2 104=Not used 105=Changeover / 6-way valve room 2 106=VAV room 2 107=EC fan room 2 |  | X | 3 | 25 | HoldingRegister | 400156 | 155 | 1
RegioAo2 | 3 | Configuration for Analog Output 2 |  | X | 3 | 26 | HoldingRegister | 400157 | 156 | 1
RegioAo3 | 6 | Configuration for Analog Output 3 |  | X | 3 | 27 | HoldingRegister | 400158 | 157 | 1
RegioAo4 |  | Configuration for Analog Output 4 |  | X | 3 | 28 | HoldingRegister | 400159 | 158 | 1
RegioDo1 | 7 | Configuration for Digital Output 1 0 =Disabled 1 =Fan speed 1 2 =Fan speed 2 3 =Fan speed 3 4 =Lighting 5 =Blind in 6 =Blind out 7 =Forced ventilation 8 =Heat valve Inc. 9 =Heat valve Dec 10=Heat valve thermal (PWM) 11=Heat valve 2 Inc. 12=Heat valve 2 Dec. 13=Heat valve 2 thermal (PWM) 14=Cool valve Inc. 15=Cool valve Dec. 16=Cool valve thermal (PWM) 20=Change over valve Inc 21=Change over valve Dec 22=Change over thermal (PWM) 23=SumAlarm 24=SumAlarm A 25=SumAlarm B 26=Heating valve extra zone, thermal (PWM) 2 27= Extra zone active signal 2 101=Fan speed 1 room 2 102=Fan speed 2 room 2 103=Fan speed 3 room 2 104=Lighting room 2 105=Blind in room 2 106=Blind out Room 2 107=Forced ventilation room 2 108=Heat Valve Inc.room 2 109=Heat Valve Dec room 2 110=Heat Valve thermal (PWM) room 2 111=Heat Valve 2 Inc. room 2 112=Heat Valve 2 Dec. room 2 113=Heat Valve 2 Thermal (PWM) room 2 114=Cool Valve Inc. room 2 115=Cool Valve Dec. room 2 116=Cool Valve thermal (PWM) room 2 120=Change over Valve Inc. room 2 121=Change over Valve Dec. room 2 122=Change over Thermal (PWM) room 2 123=SumAlarm room 2 124=SumAlarm A room 2 125=SumAlarm B room 2 126=Heating valve extra zone, thermal (PWM), room 2 2 127= Extra zone active signal, room 2 2 |  | X | 3 | 34 | HoldingRegister | 400160 | 159 | 1
RegioDo2 | 23 | Configuration for Digital Output 2 |  | X | 3 | 35 | HoldingRegister | 400161 | 160 | 1
RegioDo3 |  | Configuration for Digital Output 3 |  | X | 3 | 36 | HoldingRegister | 400162 | 161 | 1
RegioDo4 |  | Configuration for Digital Output 4 |  | X | 3 | 37 | HoldingRegister | 400163 | 162 | 1
RegioDo5 |  | Configuration for Digital Output 5 |  | X | 3 | 38 | HoldingRegister | 400164 | 163 | 1
RegioDo6 |  | Configuration for Digital Output 6 | Ardo | X | 3 | 39 | HoldingRegister | 400165 | 164 | 1
RegioHeatValve1Type |  | Output Signal for HeatValve1 0=0-10V 1=2-10V 2=10-2V 3=10-0V 4=Inc/Dec 5=PWM(Thermal) 6=6-way valve |  | X | 3 | 47 | HoldingRegister | 400166 | 165 | 1
RegioHeatValve2Type |  | Output Signal for HeatValve2: |  | X | 3 | 48 | HoldingRegister | 400167 | 166 | 1
RegioCoolValve1Type |  | Output Signal for CoolValve1: |  | X | 3 | 49 | HoldingRegister | 400168 | 167 | 1
RegioCoolValve2Type |  | Output Signal for CoolValve2: |  | X | 3 | 50 | HoldingRegister | 400169 | 168 | 1
RegioHeatCoolValveType |  | Output Signal for ChangeOver/6-way valve |  | X | 3 | 51 | HoldingRegister | 400170 | 169 | 1
RegioVAVType |  | Output Signal for VAV |  | X | 3 | 52 | HoldingRegister | 400171 | 170 | 1
RegioECFANType |  | Output Signal for EC fan |  | X | 3 | 53 | HoldingRegister | 400172 | 171 | 1
RegioUnderfloorHeatingValveType |  | Underfloor heating valve type 0=0-10 V 1=2-10V 2=10-2 V 3=10-0 V 4=NU 5=PWM (Thermal) |  | X | 3 | 54 | HoldingRegister | 400479 | 478 | 1 |  | multi_state_value 1=0-10V 2=2-10V 3=10-2V 4=10-0V 5=NU 6=PWM | 30205 |  | X
RegioHeatValve1TypeZone2 |  | Output Signal for HeatValve Room2 | Ardo | X | 3 | 57 | HoldingRegister | 400173 | 172 | 1
RegioHeatValve2TypeZone2 |  | Output Signal for HeatValve2 Room2 | Ardo | X | 3 | 58 | HoldingRegister | 400174 | 173 | 1
RegioCoolValve1TypeZone2 |  | Output Signal for CoolValve1 Room2 | Ardo | X | 3 | 59 | HoldingRegister | 400175 | 174 | 1
RegioCoolValve2TypeZone2 |  | Output Signal for CoolValve2 Room2 | Ardo | X | 3 | 60 | HoldingRegister | 400176 | 175 | 1
RegioHeatCoolValveTypeZone2 |  | Output Signal for ChangeOver/6-way valve Room2 | Ardo | X | 3 | 61 | HoldingRegister | 400177 | 176 | 1
RegioVAVTypeZone2 |  | Output Signal for VAV Room2 | Ardo | X | 3 | 62 | HoldingRegister | 400178 | 177 | 1
RegioECFANTypeZone2 |  | Output Signal for EC fan Room2 | Ardo | X | 3 | 63 | HoldingRegister | 400179 | 178 | 1
RegioUnderfloorHeatingValveTypeZone2 |  | 0=0-10V 1=2-10V 2=10-2V 3=10-0V 4=NU 5=PWM(Thermal) | Ardo | X | 3 | 64 | HoldingRegister | 400488 | 487 | 1 |  | multi_state_value 1=0-10V 2=2-10V 3=10-2V 4=10-0V 5=NU 6=PWM | 30214 |  | X
RegioValveHeat1RunTime | 120 | Run time (sec) closed to opened valve Heat 1 |  | I | 3 | 67 | HoldingRegister | 400180 | 179 | 1
RegioValveHeat2RunTime | 120 | Run time (sec) closed to opened valve Heat 2 |  | I | 3 | 69 | HoldingRegister | 400181 | 180 | 1
RegioValveCool1RunTime | 120 | Run time (sec) closed to opened valve Cool 1 |  | I | 3 | 71 | HoldingRegister | 400182 | 181 | 1
RegioValveCool2RunTime | 120 | Not used |  | I | 3 | 73 | HoldingRegister | 400183 | 182 | 1
RegioValveHeatCoolRunTime | 120 | Run time (sec) closed to opened valve HeatCool |  | I | 3 | 75 | HoldingRegister | 400184 | 183 | 1
RegioValveVAVRunTime | 120 | Run time (sec) closed to opened valve VAV |  | I | 3 | 77 | HoldingRegister | 400185 | 184 | 1
RegioValveECFanRunTime | 120 | Run time (sec) closed to opened valve ECFan |  | I | 3 | 79 | HoldingRegister | 400186 | 185 | 1
RegioValveHeat1RunTimeZone2 | 120 | Run time (sec) closed to opened valve Heat 1 Room2 | Ardo | I | 3 | 81 | HoldingRegister | 400187 | 186 | 1
RegioValveHeat2RunTimeZone2 | 120 | Run time (sec) closed to opened valve Heat 2 Room2 | Ardo | I | 3 | 83 | HoldingRegister | 400188 | 187 | 1
RegioValveCool1RunTimeZone2 | 120 | Run time (sec) closed to opened valve Cool 1 Room2 | Ardo | I | 3 | 85 | HoldingRegister | 400189 | 188 | 1
RegioValveCool2RunTimeZone2 | 120 | Not used | Ardo | I | 3 | 87 | HoldingRegister | 400190 | 189 | 1
RegioValveHeatCoolRunTimeZone2 | 120 | Run time (sec) closed to opened valve HeatCool Room2 | Ardo | I | 3 | 89 | HoldingRegister | 400191 | 190 | 1
RegioValveVAVRunTimeZone2 | 120 | Run time (sec) closed to opened valve VAV Room2 | Ardo | I | 3 | 91 | HoldingRegister | 400192 | 191 | 1
RegioValveECFanRunTimeZone2 | 120 | Run time (sec) closed to opened valve ECFan Room2 | Ardo | I | 3 | 93 | HoldingRegister | 400193 | 192 | 1
RegioCVDeadbandHeat1 | 2 | Deadband increase/decrease (%) |  | R | 3 | 101 | HoldingRegister | 400194 | 193 | 1
RegioCVDeadbandHeat2 | 2 | Deadband increase/decrease (%) |  | R | 3 | 104 | HoldingRegister | 400195 | 194 | 1
RegioCVDeadbandCool1 | 2 | Deadband increase/decrease (%) |  | R | 3 | 107 | HoldingRegister | 400196 | 195 | 1
RegioCVDeadbandCool2 | 2 | Not used |  | R | 3 | 110 | HoldingRegister | 400197 | 196 | 1
RegioCVDeadbandHeatCool | 2 | Deadband increase/decrease (%) |  | R | 3 | 113 | HoldingRegister | 400198 | 197 | 1
RegioCVDeadbandVAV | 2 | Deadband increase/decrease (%) |  | R | 3 | 116 | HoldingRegister | 400199 | 198 | 1
RegioCVDeadbandECFan | 2 | Deadband increase/decrease (%) |  | R | 3 | 120 | HoldingRegister | 400200 | 199 | 1
RegioCVDeadbandHeat1Zone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 123 | HoldingRegister | 400201 | 200 | 1
RegioCVDeadbandHeat2Zone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 126 | HoldingRegister | 400202 | 201 | 1
RegioCVDeadbandCool1Zone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 129 | HoldingRegister | 400203 | 202 | 1
RegioCVDeadbandCool2Zone2 | 2 | Not used | Ardo | R | 3 | 132 | HoldingRegister | 400204 | 203 | 1
RegioCVDeadbandHeatCoolZone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 135 | HoldingRegister | 400205 | 204 | 1
RegioCVDeadbandVAVZone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 138 | HoldingRegister | 400206 | 205 | 1
RegioCVDeadbandECFanZone2 | 2 | Deadband increase/decrease (%) Room2 | Ardo | R | 3 | 141 | HoldingRegister | 400207 | 206 | 1
Regio3PointValveStopSignal |  | If enabled it will stop the output digital signal when full open/close. The signal will stop after 1 minute of full open/ close time. This option is applied to all 3 point valves in this system. |  | L | 3 | 153 | Coil | 26 | 25
RegioPropValveHeat1PeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 163 | HoldingRegister | 400208 | 207 | 1
RegioPropValveHeat2PeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 165 | HoldingRegister | 400209 | 208 | 1
RegioPropValveCool1PeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 167 | HoldingRegister | 400210 | 209 | 1
RegioPropValveCool2PeriodTime | 210 | Not used |  | I | 3 | 169 | HoldingRegister | 400211 | 210 | 1
RegioPropValveHeatCoolPeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 171 | HoldingRegister | 400212 | 211 | 1
RegioPropValveVAVPeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 173 | HoldingRegister | 400213 | 212 | 1
RegioPropValveECFanPeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 175 | HoldingRegister | 400214 | 213 | 1
RegioPropValveHeat1PeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 177 | HoldingRegister | 400215 | 214 | 1
RegioPropValveHeat2PeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 180 | HoldingRegister | 400216 | 215 | 1
RegioPropValveCool1PeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 182 | HoldingRegister | 400217 | 216 | 1
RegioPropValveCool2PeriodTimeZone2 | 210 | Not used | Ardo | I | 3 | 184 | HoldingRegister | 400218 | 217 | 1
RegioPropValveHeatCoolPeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 186 | HoldingRegister | 400219 | 218 | 1
RegioPropValveVAVPeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 188 | HoldingRegister | 400220 | 219 | 1
RegioPropValveECFanPeriodTimeZone2 | 210 | Period time (sec) if thermal control valves Room2 | Ardo | I | 3 | 190 | HoldingRegister | 400221 | 220 | 1
RegioPropValveUnderfloorHeatingPeriodTime | 210 | Period time (sec) if thermal control valves |  | I | 3 | 192 | HoldingRegister | 400480 | 479 | 1 |  | analog_value | 30206 | seconds | X
RegioPropValveUnderfloorHeatingPeriodTimeZone2 | 210 | Period time (sec) if thermal control valves | Ardo | I | 3 | 194 | HoldingRegister | 400489 | 488 | 1 |  | analog_value | 30215 | seconds | X
RegioPropValveHeat1NCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 198 | Coil | 27 | 26
RegioPropValveHeat2NCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 199 | Coil | 28 | 27
RegioPropValveCool1NCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 200 | Coil | 29 | 28
RegioPropValveCool2NCNO |  | Not used |  | L | 3 | 201 | Coil | 30 | 29
RegioPropValveHeatCoolNCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 202 | Coil | 31 | 30
RegioPropValveVAVNCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 203 | Coil | 32 | 31
RegioPropValveECFanCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 204 | Coil | 33 | 32
RegioPropValveHeat1NCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 205 | Coil | 34 | 33
RegioPropValveHeat2NCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 206 | Coil | 35 | 34
RegioPropValveCool1NCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 207 | Coil | 36 | 35
RegioPropValveCool2NCNOZone2 |  | Not used | Ardo | L | 3 | 208 | Coil | 37 | 36
RegioPropValveHeatCoolNCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 209 | Coil | 38 | 37
RegioPropValveVAVNCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 210 | Coil | 39 | 38
RegioPropValveECFanCNOZone2 |  | Output Type (NC/NO) if thermal control valves Room2 | Ardo | L | 3 | 211 | Coil | 40 | 39
RegioPropValveUnderfloorHeatingNCNO |  | Output Type (NC/NO) if thermal control valves |  | L | 3 | 212 | Coil | 98 | 97 |  |  | binary_value | 10013 |  | X
RegioPropValveUnderfloorHeatingNCNOZone2 |  | Output Type (NC/NO) if thermal control valves | Ardo | L | 3 | 213 | Coil | 101 | 100 |  |  | binary_value | 10016 |  | X
RegioCVHeatExerciseDay | 8 | Day for exercise heating and heat/cool valve 0=Never 1-7=mon-sun 8=every day |  | X | 3 | 215 | HoldingRegister | 400222 | 221 | 1 |  | analog_value | 30062 | no_units | X
RegioCVCoolExerciseDay | 8 | Day for exercise cooling valve 0=Never 1-7=mon-sun 8=every day |  | X | 3 | 216 | HoldingRegister | 400223 | 222 | 1 |  | analog_value | 30063 | no_units | X
RegioCVHeatExerciseHour | 15 | Hour for exercise heating and heat/cool valve |  | X | 3 | 217 | HoldingRegister | 400224 | 223 | 1 |  | analog_value | 30064 | hours | X
RegioCVCoolExerciseHour | 15 | Hour for exercise cooling valve |  | X | 3 | 218 | HoldingRegister | 400225 | 224 | 1 |  | analog_value | 30065 | hours | X
RegioCVHeatExerciseMin |  | Minute for exercise heating valve |  | X | 3 | 219 | HoldingRegister | 400226 | 225 | 1
RegioCVCoolExerciseMin |  | Minute for exercise cooling valve |  | X | 3 | 220 | HoldingRegister | 400227 | 226 | 1
RegioCVHeatExerciseDayZone2 | 8 | Day for exercise heating valve Room2 0=Never 1-7=mon-sun 8=every day | Ardo | X | 3 | 221 | HoldingRegister | 400236 | 235 | 1 |  | analog_value | 30068 | no_units | X
RegioCVCoolExerciseDayZone2 | 8 | Day for exercise cooling valve Room2 0=Never 1-7=mon-sun 8=every day | Ardo | X | 3 | 222 | HoldingRegister | 400237 | 236 | 1 |  | analog_value | 30069 | no_units | X
RegioCVHeatExerciseHourZone2 | 15 | Hour for exercise heating valve Room2 | Ardo | X | 3 | 223 | HoldingRegister | 400238 | 237 | 1 |  | analog_value | 30070 | hours | X
RegioCVCoolExerciseHourZone2 | 15 | Hour for exercise cooling valve Room2 | Ardo | X | 3 | 224 | HoldingRegister | 400239 | 238 | 1 |  | analog_value | 30071 | hours | X
RegioCVHeatExerciseMinZone2 |  | Minute for exercise heating valve Room2 | Ardo | X | 3 | 225 | HoldingRegister | 400240 | 239 | 1
RegioCVCoolExerciseMinZone2 |  | Minute for exercise cooling valve Room2 | Ardo | X | 3 | 226 | HoldingRegister | 400241 | 240 | 1
RegioHeatExerciseTime | 120 | Time in seconds to Exercise the Heat Valves |  | I | 3 | 227 | HoldingRegister | 400228 | 227 | 1 |  | analog_value | 30066 | seconds | X
RegioCoolExerciseTime | 120 | Time in seconds to Exercise the Cool Valves |  | I | 3 | 229 | HoldingRegister | 400229 | 228 | 1 |  | analog_value | 30067 | seconds | X
RegioHeatExerciseTimeZone2 | 120 | Time in seconds to Exercise the Heat Valves for Room2 | Ardo | I | 3 | 231 | HoldingRegister | 400242 | 241 | 1 |  | analog_value | 30072 | seconds | X
RegioCoolExerciseTimeZone2 | 120 | Time in seconds to Exercise the Cool Valves for Room2 | Ardo | I | 3 | 233 | HoldingRegister | 400243 | 242 | 1 |  | analog_value | 30073 | seconds | X
RegioSixWayValveFirstSeqFullyOpen |  | 6-way valve tension (V) for fully open on 1st sequence |  | R | 3 | 235 | HoldingRegister | 400230 | 229 | 10
RegioSixWayValveFirstSeqStartOpen | 3.3 | 6-way valve tension (V) for start open on 1st sequence |  | R | 3 | 240 | HoldingRegister | 400231 | 230 | 10
RegioSixWayValveSecondSeqStartOpen | 6.7 | 6-way valve tension (V) for start open on 2nd sequence |  | R | 3 | 243 | HoldingRegister | 400232 | 231 | 10
RegioSixWayValveSecondSeqFullyOpen | 10 | 6-way valve tension (V) for fully open on 2nd sequence |  | R | 3 | 246 | HoldingRegister | 400233 | 232 | 10
RegioSixWayValveCenterPoint | 5 | 6-way valve tension (V) for center point |  | R | 3 | 249 | HoldingRegister | 400234 | 233 | 10
RegioSixWayValveCenterPointHyst | 2 | 6-way valve center point hysteresis (%) |  | X | 3 | 252 | HoldingRegister | 400235 | 234 | 1
RegioSixWayValveSequenceOrder |  | 6-way Valve Sequence Order 0=Heat 1st Sequence 1=Heat 2nd Sequence |  | L | 3 | 253 | Coil | 41 | 40
RegioSixWayValveFirstSeqFullyOpenZone2 |  | 6-way valve tension (V) for fully open on 1st sequence Room2 | Ardo | R | 3 | 263 | HoldingRegister | 400244 | 243 | 10
RegioSixWayValveFirstSeqStartOpenZone2 | 3.3 | 6-way valve tension (V) for start open on 1st sequence Room2 | Ardo | R | 3 | 266 | HoldingRegister | 400245 | 244 | 10
RegioSixWayValveSecondSeqStartOpenZone2 | 6.7 | 6-way valve tension (V) for start open on 2nd sequence Room2 | Ardo | R | 3 | 269 | HoldingRegister | 400246 | 245 | 10
RegioSixWayValveSecondSeqFullyOpenZone2 | 10 | 6-way valve tension (V) for fully open on 2nd sequence Room2 | Ardo | R | 3 | 272 | HoldingRegister | 400247 | 246 | 10
RegioSixWayValveCenterPointZone2 | 5 | 6-way valve tension (V) for center point Room2 | Ardo | R | 3 | 275 | HoldingRegister | 400248 | 247 | 10
RegioSixWayValveCenterPointHystZone2 | 2 | 6-way valve center point hysteresis (%) Room2 | Ardo | X | 3 | 278 | HoldingRegister | 400249 | 248 | 1
RegioSixWayValveSequenceOrderZone2 |  | 6-way Valve Sequence Order Room2 0=Heat 1st Sequence 1=Heat 2nd Sequence | Ardo | L | 3 | 279 | Coil | 42 | 41
RegioDi1NC |  | Digital input 1 function 0=Normally open 1=Normally closed |  | L | 3 | 290 | Coil | 43 | 42
RegioDi2NC |  | Digital input 2 function |  | L | 3 | 291 | Coil | 44 | 43
RegioDi3NC |  | Digital input 3 function |  | L | 3 | 292 | Coil | 45 | 44
RegioDi4NC |  | Digital input 4 function | Ardo | L | 3 | 293 | Coil | 46 | 45
RegioAi1Comp |  | Analog input 1 compensation |  | R | 3 | 304 | HoldingRegister | 400250 | 249 | 10 |  | analog_value | 30074 | degrees_celsius | X
RegioAi2Comp |  | Analog input 2 compensation |  | R | 3 | 307 | HoldingRegister | 400251 | 250 | 10 |  | analog_value | 30075 | degrees_celsius | X
RegioAi3Comp |  | Analog input 3 compensation |  | R | 3 | 310 | HoldingRegister | 400252 | 251 | 10 |  | analog_value | 30076 | degrees_celsius | X
RegioAi4Comp |  | Analog input 4 compensation | Ardo | R | 3 | 313 | HoldingRegister | 400253 | 252 | 10 |  | analog_value | 30077 | degrees_celsius | X
RegioCond_0V |  | Condense at 0 Volt input |  | R | 3 | 325 | HoldingRegister | 400254 | 253 | 1
RegioCond_10V | 100 | Condense at 10 Volt input |  | R | 3 | 328 | HoldingRegister | 400255 | 254 | 1
RegioCO2_0V |  | CO2 at 0 Volt input |  | R | 3 | 331 | HoldingRegister | 400256 | 255 | 1
RegioCO2_10V | 2000 | CO2 at 10 Volt input |  | R | 3 | 334 | HoldingRegister | 400257 | 256 | 1
RegioRH_0V |  | RH at 0 Volt input |  | R | 3 | 337 | HoldingRegister | 400258 | 257 | 1
RegioRH_10V | 100 | RH at 10 Volt input |  | R | 3 | 340 | HoldingRegister | 400259 | 258 | 1
RegioTempFilterFactor | 0.2 | Filter factor for temperature on analog input 0=no filter 1=Max filter |  | R | 3 | 343 | HoldingRegister | 400260 | 259 | 100
RegioCondFilterFactor | 0.2 | Filter factor for condense on analog input 0=no filter 1=Max filter |  | R | 3 | 346 | HoldingRegister | 400261 | 260 | 100
RegioCO2FilterFactor | 0.2 | Filter factor for CO2 on analog input 0=no filter 1=Max filter |  | R | 3 | 349 | HoldingRegister | 400262 | 261 | 100
RegioRHFilterFactor | 0.2 | Filter factor for RH on analog input 0=no filter 1=Max filter |  | R | 3 | 352 | HoldingRegister | 400263 | 262 | 100
RegioInternalTempComp |  | Internal temperature sensor compensation |  | R | 3 | 355 | HoldingRegister | 400264 | 263 | 10 |  | analog_value | 30078 | degrees_celsius | X
RegioCond_0VZone2 |  | Condense at 0 Volt input for Room2 | Ardo | R | 3 | 360 | HoldingRegister | 400265 | 264 | 1
RegioCond_10VZone2 | 100 | Condense at 10 Volt input for Room2 | Ardo | R | 3 | 363 | HoldingRegister | 400266 | 265 | 1
RegioCO2_0VZone2 |  | CO2 at 0 Volt input for Room2 | Ardo | R | 3 | 366 | HoldingRegister | 400267 | 266 | 1
RegioCO2_10VZone2 | 2000 | CO2 at 10 Volt input for Room2 | Ardo | R | 3 | 369 | HoldingRegister | 400268 | 267 | 1
RegioRH_0VZone2 |  | RH at 0 Volt input for Room2 | Ardo | R | 3 | 372 | HoldingRegister | 400269 | 268 | 1
RegioRH_10VZone2 | 100 | RH at 10 Volt input for Room2 | Ardo | R | 3 | 375 | HoldingRegister | 400270 | 269 | 1
RegioTempFilterFactorZone2 | 0.2 | Filter factor for temperature on analog input in Room2 0=no filter 1=Max filter | Ardo | R | 3 | 378 | HoldingRegister | 400271 | 270 | 100
RegioCondFilterFactorZone2 | 0.2 | Filter factor for condense on analog input in Room2 0=no filter 1=Max filter | Ardo | R | 3 | 381 | HoldingRegister | 400272 | 271 | 100
RegioCO2FilterFactorZone2 | 0.2 | Filter factor for CO2 on analog input in Room2 0=no filter 1=Max filter | Ardo | R | 3 | 384 | HoldingRegister | 400273 | 272 | 100
RegioRHFilterFactorZone2 | 0.2 | Filter factor for RH on analog input in Room2 0=no filter 1=Max filter | Ardo | R | 3 | 387 | HoldingRegister | 400274 | 273 | 100
RegioInternalTempCompZone2 |  | Internal temperature sensor compensation for Room2 | Ardo | R | 3 | 390 | HoldingRegister | 400275 | 274 | 10 |  | analog_value | 30079 | degrees_celsius | X
RegioHeat1OutputSelect | 2 | Manual/Auto of Heat1 0=Off 1=Manual 2=Auto |  | X | 3 | 394 | HoldingRegister | 400276 | 275 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30080 |  | X
RegioHeat2OutputSelect | 2 | Manual/Auto of Heat2 |  | X | 3 | 395 | HoldingRegister | 400277 | 276 | 10 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30081 |  | X
RegioCoolOutputSelect | 2 | Manual/Auto of Cool1 |  | X | 3 | 396 | HoldingRegister | 400278 | 277 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30082 |  | X
RegioHeatCoolOutputSelect | 2 | Manual/Auto of Heat Cool |  | X | 3 | 397 | HoldingRegister | 400279 | 278 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30083 |  | X
RegioVAVOutputSelect | 2 | Manual/Auto of VAV |  | X | 3 | 398 | HoldingRegister | 400280 | 279 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30084 |  | X
RegioECFanOutputSelect | 2 | Manual/Auto of ECFan |  | X | 3 | 399 | HoldingRegister | 400281 | 280 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30085 |  | X
RegioHeat1OutputSelectZone2 | 2 | Manual/Auto of Heat1 Room2 | Ardo | X | 3 | 400 | HoldingRegister | 400282 | 281 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30086 |  | X
RegioHeat2OutputSelectZone2 | 2 | Manual/Auto of Heat2 Room2 | Ardo | X | 3 | 401 | HoldingRegister | 400283 | 282 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30087 |  | X
RegioCoolOutputSelectZone2 | 2 | Manual/Auto of Cool1 Room2 | Ardo | X | 3 | 402 | HoldingRegister | 400284 | 283 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30088 |  | X
RegioHeatCoolOutputSelectZone2 | 2 | Manual/Auto of Heat Cool Room2 | Ardo | X | 3 | 403 | HoldingRegister | 400285 | 284 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30089 |  | X
RegioVAVOutputSelectZone2 | 2 | Manual/Auto of VAV Room2 | Ardo | X | 3 | 404 | HoldingRegister | 400286 | 285 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30090 |  | X
RegioECFanOutputSelectZone2 | 2 | Manual/Auto of ECFan Room2 | Ardo | X | 3 | 405 | HoldingRegister | 400287 | 286 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30091 |  | X
RegioUnderfloorHeatingSelect | 2 | Manual/Auto of Underfloor heating 0=Off 1=Manual 2=Auto |  | X | 3 | 406 | HoldingRegister | 400477 | 476 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30203 |  | X
RegioUnderfloorHeatingSelectZone2 | 2 | Manual/Auto of Underfloor heating Room2 0=Off 1=Manual 2=Auto | Ardo | X | 3 | 407 | HoldingRegister | 400486 | 485 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30212 |  | X
RegioHeat1OutputManual |  | Manual value Heat 1 |  | R | 3 | 411 | HoldingRegister | 400288 | 287 | 1 |  | analog_value | 30092 | percent | X
RegioHeat2OutputManual |  | Manual value Heat 2 |  | R | 3 | 414 | HoldingRegister | 400289 | 288 | 1 |  | analog_value | 30093 | percent | X
RegioCoolOutputManual |  | Manual value Cool |  | R | 3 | 417 | HoldingRegister | 400290 | 289 | 1 |  | analog_value | 30094 | percent | X
RegioHeatCoolOutputManual |  | Manual value Heat Cool |  | R | 3 | 420 | HoldingRegister | 400291 | 290 | 1 |  | analog_value | 30095 | percent | X
RegioVAVOutputManual |  | Manual value VAV |  | R | 3 | 423 | HoldingRegister | 400292 | 291 | 1 |  | analog_value | 30096 | percent | X
RegioECFanOutputManual |  | Manual value ECFan |  | R | 3 | 426 | HoldingRegister | 400293 | 292 | 1 |  | analog_value | 30097 | percent | X
RegioHeat1OutputManualZone2 |  | Manual value Heat 1 Room2 | Ardo | R | 3 | 429 | HoldingRegister | 400294 | 293 | 1 |  | analog_value | 30098 | percent | X
RegioHeat2OutputManualZone2 |  | Manual value Heat 2 Room2 | Ardo | R | 3 | 432 | HoldingRegister | 400295 | 294 | 1 |  | analog_value | 30099 | percent | X
RegioCoolOutputManualZone2 |  | Manual value Cool Room2 | Ardo | R | 3 | 435 | HoldingRegister | 400296 | 295 | 1 |  | analog_value | 30100 | percent | X
RegioHeatCoolOutputManualZone2 |  | Manual value Heat Cool Room2 | Ardo | R | 3 | 438 | HoldingRegister | 400297 | 296 | 1 |  | analog_value | 30101 | percent | X
RegioVAVOutputManualZone2 |  | Manual value VAV Room2 | Ardo | R | 3 | 441 | HoldingRegister | 400298 | 297 | 1 |  | analog_value | 30102 | percent | X
RegioECFanOutputManualZone2 |  | Manual value ECFan Room2 | Ardo | R | 3 | 444 | HoldingRegister | 400299 | 298 | 1 |  | analog_value | 30103 | percent | X
RegioUnderfloorHeatingManualValue |  | Manual Value Underfloor heating |  | R | 3 | 447 | HoldingRegister | 400478 | 477 | 1 |  | analog_value | 30204 | percent | X
RegioUnderfloorHeatingManualValueZone2 |  | Manual Value Underfloor heating | Ardo | R | 3 | 450 | HoldingRegister | 400487 | 486 | 1 |  | analog_value | 30213 | percent | X
RegioLightSelect | 2 | Manual/Auto of Lighting 0=Off 1=On 2=Auto |  | X | 3 | 454 | HoldingRegister | 400300 | 299 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30104 |  | X
RegioSunBlindsInSelect | 2 | Manual/Auto of BlindIn |  | X | 3 | 455 | HoldingRegister | 400301 | 300 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30105 |  | X
RegioSunBlindsOutSelect | 2 | Manual/Auto of BlindOut |  | X | 3 | 456 | HoldingRegister | 400302 | 301 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30106 |  | X
RegioForcedVentSelect | 2 | Manual/Auto of ForceVentilation |  | X | 3 | 457 | HoldingRegister | 400303 | 302 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30107 |  | X
RegioDigOutSelectSumAlarm | 2 | Manual/Auto of SumAlarm |  | X | 3 | 458 | HoldingRegister | 400304 | 303 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30108 |  | X
RegioDigOutSelectSumAlarmA | 2 | Manual/Auto of SumAlarmA |  | X | 3 | 459 | HoldingRegister | 400305 | 304 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30109 |  | X
RegioDigOutSelectSumAlarmB | 2 | Manual/Auto of SumAlarmB |  | X | 3 | 460 | HoldingRegister | 400306 | 305 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30110 |  | X
RegioLightSelectZone2 | 2 | Manual/Auto of Lighting Room2 | Ardo | X | 3 | 461 | HoldingRegister | 400307 | 306 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30111 |  | X
RegioSunBlindsInSelectZone2 | 2 | Manual/Auto of BlindIn Room2 | Ardo | X | 3 | 462 | HoldingRegister | 400308 | 307 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30112 |  | X
RegioSunBlindsOutSelectZone2 | 2 | Manual/Auto of BlindOut Room2 | Ardo | X | 3 | 463 | HoldingRegister | 400309 | 308 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30113 |  | X
RegioForcedVentSelectZone2 | 2 | Manual/Auto of ForceVentilation Room2 | Ardo | X | 3 | 464 | HoldingRegister | 400310 | 309 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30114 |  | X
RegioDigOutSelectSumAlarmZone2 | 2 | Manual/Auto of SumAlarm Room2 | Ardo | X | 3 | 465 | HoldingRegister | 400311 | 310 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30115 |  | X
RegioDigOutSelectSumAlarmAZone2 | 2 | Manual/Auto of SumAlarmA Room2 | Ardo | X | 3 | 466 | HoldingRegister | 400312 | 311 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30116 |  | X
RegioDigOutSelectSumAlarmBZone2 | 2 | Manual/Auto of SumAlarmB Room2 | Ardo | X | 3 | 467 | HoldingRegister | 400313 | 312 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30117 |  | X
RegioFanSelect | 4 | Fan speed Selected Remote/RegioTool 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Auto |  | X | 3 | 472 | HoldingRegister | 400314 | 313 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 5=Speed4 6=Auto | 30118 |  | X
RegioFanSelectZone2 | 4 | Fan speed Selected Remote/RegioTool, room 2 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Auto | Ardo | X | 3 | 473 | HoldingRegister | 400315 | 314 | 1 |  | multi_state_value 1=Off 2=Speed1 3=Speed2 4=Speed3 5=Speed4 6=Auto | 30119 |  | X
RegioControllerMode | 9 | Control Mode 0=Heating 1=Heating + Heating 2=Heating + Cooling 3=Cooling 4=Heating/Cooling (change-over) 5=Heating + Heating/Cooling (change-over) 6=Heating + VAV 7=Cooling + VAV 8=VAV 9=Heating + Cooling + VAV |  | X | 3 | 489 | HoldingRegister | 400002 | 1 | 1 |  | multi_state_value 1=Heat 2=Heat/Heat 3=Heat/Cool 4=Cool 5=Heat/Cool via C/O 6=Heat/Heat/Cool via C/O 7=Heat/VAV 8=Cool/VAV 9=VAV 10=Heat/Cool/VAV | 40001
RegioControllerModeZone2 | 9 | Control Mode Room2 0=Heating 1=Heating + Heating 2=Heating + Cooling 3=Cooling 4=Heating/Cooling (change-over) 5=Heating + Heating/Cooling (change-over) 6=Heating + VAV 7=Cooling + VAV 8=VAV 9=Heating + Cooling + VAV | Ardo | X | 3 | 490 | HoldingRegister | 400074 | 73 | 1 |  | multi_state_value 1=Heat 2=Heat/Heat 3=Heat/Cool 4=Cool 5=Heat/Cool via C/O 6=Heat/Heat/Cool via C/O 7=Heat/VAV 8=Cool/VAV 9=VAV 10=Heat/Cool/VAV | 40002
RegioEnableZone2 |  | Enables Control in Room2 | Ardo | L | 3 | 491 | Coil | 14 | 13
RegioHeatSequenceOrder |  | Y1 and Y2 for Heat/Heat 0=Y1 before Y2 1=Y2 before Y1 |  | L | 3 | 492 | Coil | 2 | 1
RegioCoolSequenceOrder |  | Y2 and Y3 for Heat/Cool/VAV 0=Y2 beforeY3 1=Y3 before Y2 |  | L | 3 | 493 | Coil | 3 | 2
RegioHeatSequenceOrderZone2 |  | Y1 and Y2 for Heat/Heat Room2 0=Y1 before Y2 1=Y2 before Y1 | Ardo | L | 3 | 494 | Coil | 15 | 14
RegioCoolSequenceOrderZone2 |  | Y2 and Y3 for Heat/Cool/VAV Room2 0=Y2 beforeY3 1=Y3 before Y2 | Ardo | L | 3 | 495 | Coil | 16 | 15
RegioVAVControlType | 2 | Control the VAV output 0=By temperature 2=By CO2 level 3=By both, the highest need |  | X | 3 | 496 | HoldingRegister | 400110 | 109 | 1
RegioVAVControlTypeZone2 | 2 | Control the VAVoutput Room2 0=By temperature 2=By CO2 level 3=By both, the highest need | Ardo | X | 3 | 497 | HoldingRegister | 400111 | 110 | 1
RegioHeatSetPointOccupied | 22 | Room Base setpoint heating |  | R | 3 | 516 | HoldingRegister | 400003 | 2 | 10 |  | analog_value | 30001 | degrees_celsius | X
RegioCoolSetPointOccupied | 24 | Room Base setpoint cooling |  | R | 3 | 519 | HoldingRegister | 400004 | 3 | 10 |  | analog_value | 30002 | degrees_celsius | X
RegioSetPointDeadBandStandby | 3 | Deadband in Standby mode |  | R | 3 | 522 | HoldingRegister | 400009 | 8 | 10 |  | analog_value | 30007 | degrees_celsius | X
RegioHeatSetPointUnoccupied | 15 | Setpoint heating in Unoccupied |  | R | 3 | 525 | HoldingRegister | 400007 | 6 | 10 |  | analog_value | 30005 | degrees_celsius | X
RegioCoolSetPointUnoccupied | 30 | Setpoint Cooling in Unoccupied |  | R | 3 | 528 | HoldingRegister | 400008 | 7 | 10 |  | analog_value | 30006 | degrees_celsius | X
RegioFrostProtectionSetPoint | 8 | Setpoint frostprotection |  | R | 3 | 531 | HoldingRegister | 400010 | 9 | 10 |  | analog_value | 30008 | degrees_celsius | X
RegioRUSetPointAdjPos | 3 | Max allowed offset over setpoint |  | R | 3 | 534 | HoldingRegister | 400011 | 10 | 1
RegioRUSetPointAdjNeg | 3 | Max allowed offset below setpoint |  | R | 3 | 537 | HoldingRegister | 400012 | 11 | 1
RegioSetPOffset |  | not used |  | R | 3 | 540 | HoldingRegister | 400013 | 12 | 10
RegioSetPOffsetRemote |  | Setpoint Offset Remote1 |  | R | 3 | 543 | HoldingRegister | 400014 | 13 | 10 |  | analog_value | 30009 | degrees_celsius | X
RegioHeatSetPointOccupiedZone2 | 22 | Room Base setpoint heating Room2 | Ardo | R | 3 | 546 | HoldingRegister | 400075 | 74 | 10 |  | analog_value | 30033 | degrees_celsius | X
RegioCoolSetPointOccupiedZone2 | 24 | Room Base setpoint cooling Room2 | Ardo | R | 3 | 549 | HoldingRegister | 400076 | 75 | 10 |  | analog_value | 30034 | degrees_celsius | X
RegioSetPointDeadBandStandbyZone2 | 3 | Deadband in Standby mode Room2 | Ardo | R | 3 | 552 | HoldingRegister | 400081 | 80 | 10 |  | analog_value | 30039 | degrees_celsius | X
RegioHeatSetPointUnoccupiedZone2 | 15 | Setpoint heating in Unoccupied Room2 | Ardo | R | 3 | 555 | HoldingRegister | 400079 | 78 | 10 |  | analog_value | 30037 | degrees_celsius | X
RegioCoolSetPointUnoccupiedZone2 | 30 | Setpoint Cooling in Unoccupied Room2 | Ardo | R | 3 | 558 | HoldingRegister | 400080 | 79 | 10 |  | analog_value | 30038 | degrees_celsius | X
RegioFrostProtectionSetPointZone2 | 8 | Setpoint frostprotection Room2 | Ardo | R | 3 | 561 | HoldingRegister | 400082 | 81 | 10 |  | analog_value | 30040 | degrees_celsius | X
RegioRUSetPointAdjPosZone2 | 3 | Max allowed offset over setpoint Room2 | Ardo | R | 3 | 564 | HoldingRegister | 400083 | 82 | 1
RegioRUSetPointAdjNegZone2 | 3 | Max allowed offset below setpoint Room2 | Ardo | R | 3 | 567 | HoldingRegister | 400084 | 83 | 1
RegioSetPOffsetZone2 |  | not used | Ardo | R | 3 | 570 | HoldingRegister | 400085 | 84 | 10
RegioSetPOffsetRemoteZone2 |  | Setpoint Offset remote Zone 2 1 | Ardo | R | 3 | 573 | HoldingRegister | 400086 | 85 | 10 |  | analog_value | 30041 | degrees_celsius | X
RegioHeatOutputMinLimit |  | Min Limit for Heat Output |  | R | 3 | 588 | HoldingRegister | 400022 | 21 | 1
RegioHeatOutputMaxLimit | 100 | Max Limit for Heat Output |  | R | 3 | 591 | HoldingRegister | 400023 | 22 | 1
RegioHeat2OutputMinLimit |  | Min Limit for Heat Output |  | R | 3 | 594 | HoldingRegister | 400024 | 23 | 1
RegioHeat2OutputMaxLimit | 100 | Max Limit for Heat Output |  | R | 3 | 597 | HoldingRegister | 400025 | 24 | 1
RegioCool1OutputMinLimit |  | Min Limit for Cool Output |  | R | 3 | 600 | HoldingRegister | 400026 | 25 | 1
RegioCool1OutputMaxLimit | 100 | Max Limit for Cool Output |  | R | 3 | 603 | HoldingRegister | 400027 | 26 | 1
RegioCool2OutputMinLimit |  | Not used |  | R | 3 | 606 | HoldingRegister | 400028 | 27 | 1
RegioCool2OutputMaxLimit | 100 | Not used |  | R | 3 | 609 | HoldingRegister | 400029 | 28 | 1
RegioVAVOutputMinLimitOff |  | Min Limit for VAV Output at off State |  | R | 3 | 612 | HoldingRegister | 400030 | 29 | 1 |  | analog_value | 30012 | percent | X
RegioVAVOutputMinLimitUno | 10 | Min Limit for VAV Output at Unoccupied State |  | R | 3 | 615 | HoldingRegister | 400031 | 30 | 1 |  | analog_value | 30013 | percent | X
RegioVAVOutputMinLimitStandby | 10 | Min Limit for VAV Output at Standby State |  | R | 3 | 618 | HoldingRegister | 400032 | 31 | 1 |  | analog_value | 30014 | percent | X
RegioVAVOutputMinLimitOcc | 20 | Min Limit for VAV Output at Occupied or Bypass State |  | R | 3 | 621 | HoldingRegister | 400033 | 32 | 1 |  | analog_value | 30015 | percent | X
RegioVAVOutputMaxLimit | 100 | Max Limit for VAV Output |  | R | 3 | 624 | HoldingRegister | 400034 | 33 | 1 |  | analog_value | 30016 | percent | X
RegioHeatOutputMinLimitZone2 |  | Min Limit for Heat Output Room2 | Ardo | R | 3 | 627 | HoldingRegister | 400094 | 93 | 1
RegioHeatOutputMaxLimitZone2 | 100 | Max Limit for Heat Output Room2 | Ardo | R | 3 | 630 | HoldingRegister | 400095 | 94 | 1
RegioHeat2OutputMinLimitZone2 |  | Min Limit for Heat Output Room2 | Ardo | R | 3 | 633 | HoldingRegister | 400096 | 95 | 1
RegioHeat2OutputMaxLimitZone2 | 100 | Max Limit for Heat Output Room2 | Ardo | R | 3 | 636 | HoldingRegister | 400097 | 96 | 1
RegioCool1OutputMinLimitZone2 |  | Min Limit for Cool Output Room2 | Ardo | R | 3 | 639 | HoldingRegister | 400098 | 97 | 1
RegioCool1OutputMaxLimitZone2 | 100 | Max Limit for Cool Output Room2 | Ardo | R | 3 | 642 | HoldingRegister | 400099 | 98 | 1
RegioCool2OutputMinLimitZone2 |  | Not used | Ardo | R | 3 | 645 | HoldingRegister | 400100 | 99 | 1
RegioCool2OutputMaxLimitZone2 | 100 | Not used | Ardo | R | 3 | 648 | HoldingRegister | 400101 | 100 | 1
RegioVAVOutputMinLimitOffZone2 |  | Min Limit for VAV Output at off State Room2 | Ardo | R | 3 | 651 | HoldingRegister | 400102 | 101 | 1 |  | analog_value | 30044 | percent | X
RegioVAVOutputMinLimitUnoZone2 | 10 | Min Limit for VAV Output at Unoccupied State Room2 | Ardo | R | 3 | 654 | HoldingRegister | 400103 | 102 | 1 |  | analog_value | 30045 | percent | X
RegioVAVOutputMinLimitStandbyZone2 | 10 | Min Limit for VAV Output at Standby State Room2 | Ardo | R | 3 | 657 | HoldingRegister | 400104 | 103 | 1 |  | analog_value | 30046 | percent | X
RegioVAVOutputMinLimitOccZone2 | 20 | Min Limit for VAV Output at Occupied or Bypass State Room2 | Ardo | R | 3 | 660 | HoldingRegister | 400105 | 104 | 1 |  | analog_value | 30047 | percent | X
RegioVAVOutputMaxLimitZone2 | 100 | Max Limit for VAV Output Room2 | Ardo | R | 3 | 663 | HoldingRegister | 400106 | 105 | 1 |  | analog_value | 30048 | percent | X
RegioMaxAirFlowHeatDemand |  | Max Airflow on Heat Demand , if above 0% the max airflow function is enabled |  | R | 3 | 681 | HoldingRegister | 400039 | 38 | 1
RegioMaxAirflowHeatDemandZone2 |  | Max Airflow on Heat Demand , if above 0% the max airflow function is enabled Room2 | Ardo | R | 3 | 684 | HoldingRegister | 400107 | 106 | 1
RegioForcedVentControlMode | 3 | Forced Ventilation Control Mode 0=Off 1=Force Vent on Heat 2=Force Vent on Cool 3=Force Vent on Both Heat and Cool |  | X | 3 | 693 | HoldingRegister | 400040 | 39 | 1
RegioForcedVentSequence |  | ForcedVentSequence 0=Forced Ventilation Just 2nd sequence 1=Force Ventilation both sequences |  | L | 3 | 694 | Coil | 5 | 4
RegioForcedVentAtMaxOutput |  | Forced Ventilation on Max Heat/Cool/Both 0=Off 1=Forced Ventilation on Max Heat 2=Forced Ventilation on Max Cool 3=Forced Ventilation on Max Heat or Cool |  | X | 3 | 695 | HoldingRegister | 400041 | 40 | 1
RegioForcedVentControlModeZone2 | 3 | Forced Ventilation Control Mode Room2 0=Off 1=Force Vent on Heat 2=Force Vent on Cool 3=Force Vent on Both Heat and Cool | Ardo | X | 3 | 696 | HoldingRegister | 400108 | 107 | 1
RegioForcedVentSequenceZone2 |  | ForcedVentSequence Room2 0=Forced Ventilation Just 2nd sequence 1=Force Ventilation both sequences Room2 | Ardo | L | 3 | 697 | Coil | 17 | 16
RegioForcedVentAtMaxOutputZone2 |  | Forced Ventilation on Max Heat/Cool/Both Room2 0=Off 1=Forced Ventilation on Max Heat 2=Forced Ventilation on Max Cool 3=Forced Ventilation on Max Heat or Cool | Ardo | X | 3 | 698 | HoldingRegister | 400109 | 108 | 1
RegioRoomTempPBand | 10 | Temperature PID P Band |  | R | 3 | 708 | HoldingRegister | 400005 | 4 | 1 |  | analog_value | 30003 | no_units | X
RegioRoomTempITime | 300 | Temperature PID I Time |  | R | 3 | 711 | HoldingRegister | 400006 | 5 | 1 |  | analog_value | 30004 | seconds | X
RegioRoomTempPBandZone2 | 10 | Temperature PID P Band Room2 | Ardo | R | 3 | 714 | HoldingRegister | 400077 | 76 | 1 |  | analog_value | 30035 | no_units | X
RegioRoomTempITimeZone2 | 300 | Temperature PID I Time Room2 | Ardo | R | 3 | 717 | HoldingRegister | 400078 | 77 | 1 |  | analog_value | 30036 | seconds | X
RegioSupplyAirTempLimCascadeFactor | 3 | Cascade Factor for the Cascade PID |  | R | 3 | 729 | HoldingRegister | 400042 | 41 | 1 |  | analog_value | 30020 | no_units | X
RegioSupplyAirTempLimHeatMinLimit | 24 | Min Setpoint for the Cascade PID in Heat Mode |  | R | 3 | 732 | HoldingRegister | 400043 | 42 | 1 |  | analog_value | 30021 | degrees_celsius | X
RegioSupplyAirTempLimHeatMaxLimit | 35 | Max Setpoint for the Cascade PID in Heat Mode |  | R | 3 | 735 | HoldingRegister | 400044 | 43 | 1 |  | analog_value | 30022 | degrees_celsius | X
RegioSupplyAirTempLimCoolMinLimit | 12 | Min Setpoint for the Cascade PID in Cool Mode |  | R | 3 | 738 | HoldingRegister | 400045 | 44 | 1 |  | analog_value | 30023 | degrees_celsius | X
RegioSupplyAirTempLimCoolMaxLimit | 24 | Max Setpoint for the Cascade PID in Cool Mode |  | R | 3 | 741 | HoldingRegister | 400046 | 45 | 1 |  | analog_value | 30024 | degrees_celsius | X
RegioSupplyAirTempLimFrostProtSetPoint | 8 | Supply Air Temp Frost Protection Temperature |  | R | 3 | 744 | HoldingRegister | 400047 | 46 | 1 |  | analog_value | 30025 | degrees_celsius | X
RegioSupplyAirTempLimCascadeFactorZone2 | 3 | Cascade Factor for the Cascade PID Room2 | Ardo | R | 3 | 748 | HoldingRegister | 400112 | 111 | 1 |  | analog_value | 30049 | no_units | X
RegioSupplyAirTempLimHeatMinLimitZone2 | 24 | Min Setpoint for the Cascade PID in Heat Mode Room2 | Ardo | R | 3 | 751 | HoldingRegister | 400113 | 112 | 1 |  | analog_value | 30050 | degrees_celsius | X
RegioSupplyAirTempLimHeatMaxLimitZone2 | 35 | Max Setpoint for the Cascade PID in Heat Mode Room2 | Ardo | R | 3 | 754 | HoldingRegister | 400114 | 113 | 1 |  | analog_value | 30051 | degrees_celsius | X
RegioSupplyAirTempLimCoolMinLimitZone2 | 12 | Min Setpoint for the Cascade PID in Cool Mode Room2 | Ardo | R | 3 | 757 | HoldingRegister | 400115 | 114 | 1 |  | analog_value | 30052 | degrees_celsius | X
RegioSupplyAirTempLimCoolMaxLimitZone2 | 24 | Max Setpoint for the Cascade PID in Cool Mode Room2 | Ardo | R | 3 | 760 | HoldingRegister | 400116 | 115 | 1 |  | analog_value | 30053 | degrees_celsius | X
RegioSupplyAirTempLimFrostProtSetPointZone2 | 8 | Supply Air Temp Frost Protection Temperature Room2 | Ardo | R | 3 | 763 | HoldingRegister | 400117 | 116 | 1 |  | analog_value | 30054 | degrees_celsius | X
RegioCO2PBand | 100 | CO2 PID P Band |  | R | 3 | 776 | HoldingRegister | 400048 | 47 | 1 |  | analog_value | 30026 | no_units | X
RegioCO2ITime | 100 | CO2 PID I Time |  | R | 3 | 780 | HoldingRegister | 400049 | 48 | 1 |  | analog_value | 30027 | seconds | X
RegioCO2FirstSequence |  | If enabled in modes 7,8 (cool/cool and heat/cool/vav) the CO2 output will override both outputs if the actual output is lower than the CO2 Output by default it only overrides the second sequence |  | L | 3 | 783 | Coil | 6 | 5
RegioCO2SetPoint | 600 | Setpoint for CO2 PI Controller in PPM |  | R | 3 | 784 | HoldingRegister | 400050 | 49 | 1 |  | analog_value | 30028 | parts_per_million | X
RegioCO2PBandZone2 | 100 | CO2 PID P Gain Room2 | Ardo | R | 3 | 787 | HoldingRegister | 400118 | 117 | 1 |  | analog_value | 30055 | no_units | X
RegioCO2ITimeZone2 | 100 | CO2 PID I Time Room2 | Ardo | R | 3 | 790 | HoldingRegister | 400119 | 118 | 1 |  | analog_value | 30056 | seconds | X
RegioCO2FirstSequenceZone2 |  | If enabled in modes 7,8 (cool/cool and heat/cool/vav) the CO2 output will override both outputs if the actual output is lower than the CO2 Output by default it only overrides the second sequence Room2 | Ardo | L | 3 | 793 | Coil | 18 | 17
RegioCO2SetpointZone2 | 600 | Setpoint for CO2 PI Controller in PPM Room2 | Ardo | R | 3 | 794 | HoldingRegister | 400120 | 119 | 1 |  | analog_value | 30057 | parts_per_million | X
RegioCO2PresenceDetection | 1 | Activate presence on CO2 |  | L | 3 | 806 | Coil | 7 | 6
RegioCO2PresenceLimit | 800 | Activate presence if CO2 is higher |  | R | 3 | 807 | HoldingRegister | 400051 | 50 | 1
RegioCO2PresenceHyst | 160 | Diff for deactivate presence on CO2 |  | R | 3 | 810 | HoldingRegister | 400052 | 51 | 1
RegioCO2PresenceDetectionZone2 | 1 | Activate presence on CO2 Room2 | Ardo | L | 3 | 813 | Coil | 19 | 18
RegioCO2PresenceLimitZone2 | 800 | Activate presence if CO2 is higher Room2 | Ardo | R | 3 | 814 | HoldingRegister | 400121 | 120 | 1
RegioCO2PresenceHystZone2 | 160 | Diff for deactivate presence on CO2 Room2 | Ardo | R | 3 | 817 | HoldingRegister | 400122 | 121 | 1
RegioFanControlMode |  | FanControl Mode 0=No control 1=Controlled by Heating 2=Controlled by cooling 3=Controlled by both heat and cooling |  | X | 3 | 829 | HoldingRegister | 400053 | 52 | 1
RegioFanSpeed1Start | 20 | If higher controller output start fan speed 1 |  | X | 3 | 830 | HoldingRegister | 400054 | 53 | 1
RegioFanSpeed2Start | 60 | If higher controller output start fan speed 2 |  | X | 3 | 831 | HoldingRegister | 400055 | 54 | 1
RegioFanSpeed3Start | 100 | If higher controller output start fan speed 3 |  | X | 3 | 832 | HoldingRegister | 400056 | 55 | 1
RegioFanSpeedHyst | 5 | Hysteresis % for start/stop fan |  | X | 3 | 833 | HoldingRegister | 400057 | 56 | 1
RegioRUNoOfFanSpeeds | 3 | Configured number of fan speeds (1-3) |  | X | 3 | 834 | HoldingRegister | 400058 | 57 | 1
RegioMinFanSpeed |  | Min Speed for the fan (0-Stop 1-Speed 1) |  | L | 3 | 835 | Coil | 8 | 7
RegioFanSwitchTime | 2 | Time (sec) before switching fan speed when changed from RU |  | I | 3 | 836 | HoldingRegister | 400059 | 58 | 1
RegioECFanMaxLimit | 100 | Max limit for the EC fan (0-100) |  | R | 3 | 840 | HoldingRegister | 400060 | 59 | 1
RegioECFanMinLimit | 10 | Min limit for the EC fan (0-100) |  | R | 3 | 843 | HoldingRegister | 400061 | 60 | 1
RegioECFanStartSpeed | 15 | The fan will start at this speed when demand is over the fan speed demand. |  | R | 3 | 846 | HoldingRegister | 400062 | 61 | 1
RegioFanTypeSelector |  | Type of Fan used , needed for display purposes in the RU. 0=3Speed Fan 1=EC Fan |  | L | 3 | 849 | Coil | 9 | 8
RegioFanAfterBlowControl |  | If enabled the Fan will work FanStopTime after Heat applied 0=Off 1=Heat1 2=Heat2 3=Heat1 or Heat2 |  | X | 3 | 850 | HoldingRegister | 400064 | 63 | 1
RegioFanAfterBlowMinSpeed |  | Minimum Fan Speed when FanafterBlow Active |  | X | 3 | 851 | HoldingRegister | 400065 | 64 | 1 |  | multi_state_value 1=Off 2=1 3=2 4=3 | 30030 |  | X
RegioFanStopTime | 120 | Time (Sec) for the Fan Stop delay when Fan AfterBlow used |  | I | 3 | 852 | HoldingRegister | 400063 | 62 | 1 |  | analog_value | 30029 | seconds | X
RegioKickStartTime |  | Time (Sec) to Kick Start the Fan, during this time the fan will work at 100%. If 0 this function is not active |  | I | 3 | 854 | HoldingRegister | 400066 | 65 | 1
RegioFanControlModeZone2 |  | FanControl Mode Room2 0=No control 1=Controlled by Heating 2=Controlled by cooling 3=Controlled by both heat and cooling | Ardo | X | 3 | 856 | HoldingRegister | 400123 | 122 | 1
RegioFanSpeed1StartZone2 | 20 | If higher controller output start fan speed 1 Room2 | Ardo | X | 3 | 857 | HoldingRegister | 400124 | 123 | 1
RegioFanSpeed2StartZone2 | 60 | If higher controller output start fan speed 2 Room2 | Ardo | X | 3 | 858 | HoldingRegister | 400125 | 124 | 1
RegioFanSpeed3StartZone2 | 100 | If higher controller output start fan speed 3 Room2 | Ardo | X | 3 | 859 | HoldingRegister | 400126 | 125 | 1
RegioFanSpeedHystZone2 | 5 | Hysteresis % for start/stop fan Room2 | Ardo | X | 3 | 860 | HoldingRegister | 400127 | 126 | 1
RegioRUNoOfFanSpeedsZone2 | 3 | Configured number of fan speeds (1-3) Room2 | Ardo | X | 3 | 861 | HoldingRegister | 400128 | 127 | 1
RegioMinFanSpeedZone2 |  | Min Speed for the fan Room2: 0-=Stop 1=Speed 1 | Ardo | L | 3 | 862 | Coil | 20 | 19
RegioFanSwitchTimeZone2 | 2 | Time (sec) before switching fan speed when changed from RU Room2 | Ardo | I | 3 | 863 | HoldingRegister | 400129 | 128 | 1
RegioECFanMaxLimitZone2 | 100 | Max limit for the EC fan (0-100) Room2 | Ardo | R | 3 | 865 | HoldingRegister | 400130 | 129 | 1
RegioECFanMinLimitZone2 | 10 | Min limit for the EC fan (0-100) Room2 | Ardo | R | 3 | 868 | HoldingRegister | 400131 | 130 | 1
RegioECFanStartSpeedZone2 | 15 | The fan will start at this speed when demand is over the fan speed demand, Room2 | Ardo | R | 3 | 871 | HoldingRegister | 400132 | 131 | 1
RegioFanTypeSelectorZone2 |  | Type of Fan used , needed for display purposes in the RU Room2 0=3 Speed Fan 1=EC fan | Ardo | L | 3 | 874 | Coil | 21 | 20
RegioFanAfterBlowControlZone2 |  | If enabled the Fan will work FanStopTime after Heat applied, Room2 0=Off 1=Heat1 2=Heat2 3=Heat1 or Heat2 | Ardo | X | 3 | 875 | HoldingRegister | 400134 | 133 | 1
RegioFanAfterBlowMinSpeedZone2 |  | Minimum Fan Speed when FanafterBlow Active, Room2 | Ardo | X | 3 | 876 | HoldingRegister | 400135 | 134 | 1 |  | multi_state_value 1=Off 2=1 3=2 4=3 | 30059 |  | X
RegioFanStopTimeZone2 | 120 | Time (Sec) for the Fan Stop delay when Fan After- Blow used, Room2 | Ardo | I | 3 | 877 | HoldingRegister | 400133 | 132 | 1 |  | analog_value | 30058 | seconds | X
RegioKickStartTimeZone2 |  | Time (Sec) to Kick Start the Fan for Room2, during this time the fan will work at 100%. If 0 this function is not active | Ardo | I | 3 | 879 | HoldingRegister | 400136 | 135 | 1
RegioBoostMode | 2 | Boost Function will work when on Heating (0) Cooling (1) Both (2) |  | X | 3 | 899 | HoldingRegister | 400067 | 66 | 1
RegioConfigFanBoostTime |  | Time (sec) [0 to 600 seconds] that the Boost Function is active. If 0 the boost function is disabled |  | I | 3 | 900 | HoldingRegister | 400068 | 67 | 1
RegioShortStart | 10 | Time (sec) that the Fan runs in Max Speed |  | I | 3 | 902 | HoldingRegister | 400069 | 68 | 1
RegioBoostPBand | 5 | P-band of the P-Controller of the Fan (just in Boost Startup Mode) |  | R | 3 | 904 | HoldingRegister | 400070 | 69 | 1
RegioBoostModeZone2 | 2 | Boost Function will work when on Room2 0=Heating 1=Cooling 2=Both | Ardo | X | 3 | 907 | HoldingRegister | 400137 | 136 | 1
RegioConfigFanBoostTimeZone2 |  | Time (sec) [0 to 600 seconds] that the Boost Function is active. If 0 the boost function is disabled Room2 | Ardo | I | 3 | 908 | HoldingRegister | 400138 | 137 | 1
RegioShortStartZone2 | 10 | Time (sec) that the Fan runs in Max Speed Room2 | Ardo | I | 3 | 910 | HoldingRegister | 400139 | 138 | 1
RegioBoostPBandZone2 | 5 | P-band of the P-Controller of the Fan (just in Boost Startup Mode) Room2 | Ardo | R | 3 | 912 | HoldingRegister | 400140 | 139 | 1
RegioControllerStateReturn | 3 | Select return unit state 0=Off 1=Unoccupied 2=Stand-by 3=Occupied |  | X | 3 | 924 | HoldingRegister | 400015 | 14 | 1
RegioControllerStateShutDown | 1 | Select shutdown state 0=Off 1=Unoccupied 2=Stand-by 3=Occupied |  | X | 3 | 925 | HoldingRegister | 400016 | 15 | 1
RegioControllerStatePresence | 4 | Presence operating mode 3=Occupied 4=Bypass |  | X | 3 | 926 | HoldingRegister | 400017 | 16 | 1
RegioControllerStateRemote | 5 | Is used for remote control 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 5=No remote control |  | X | 3 | 927 | HoldingRegister | 400018 | 17 | 1 |  | multi_state_value 1=Off 2=Unoccupied 3=Stand-by 4=Occupied 5=Not Used 6=No remote control | 30010 |  | X
RegioControllerStateBypassTime | 120 | Time for Bypass mode (Min) |  | I | 3 | 930 | HoldingRegister | 400019 | 18 | 1 |  | analog_value | 30011 | minutes | X
RegioPresenceOffDelay | 10 | Off timer for changing to not presence (min) |  | I | 3 | 932 | HoldingRegister | 400020 | 19 | 1
RegioPresenceOnDelay |  | On timer for changing to presence (min) |  | I | 3 | 934 | HoldingRegister | 400021 | 20 | 1
RegioControllerStateReturnZone2 | 3 | Select return unit state Room2 0=Off 1=Unoccupied 2=Stand-by 3=Occupied | Ardo | X | 3 | 936 | HoldingRegister | 400087 | 86 | 1
RegioControllerStateShutDownZone2 | 1 | Select shutdown state Room2 0=Off 1=Unoccupied 2=Stand-by 3=Occupied | Ardo | X | 3 | 937 | HoldingRegister | 400088 | 87 | 1
RegioControllerStatePresenceZone2 | 4 | Presence operating mode Room2 3=Occupied 4=Bypass | Ardo | X | 3 | 938 | HoldingRegister | 400089 | 88 | 1
RegioControllerStateRemoteZone2 | 5 | Is used for remote control Room2 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 5=No remote control | Ardo | X | 3 | 939 | HoldingRegister | 400090 | 89 | 1 |  | multi_state_value 1=Off 2=Unoccupied 3=Stand-by 4=Occupied 5=Not Used 6=No remote control | 30042 |  | X
RegioControllerStateBypassTimeZone2 | 120 | Time for Bypass mode (Min) Room2 | Ardo | I | 3 | 942 | HoldingRegister | 400091 | 90 | 1 |  | analog_value | 30043 | minutes | X
RegioPresenceOffDelayZone2 | 10 | Off timer for changing to not presence (min) Room2 | Ardo | I | 3 | 944 | HoldingRegister | 400092 | 91 | 1
RegioPresenceOnDelayZone2 |  | On timer for changing to presence (min) Room2 | Ardo | I | 3 | 946 | HoldingRegister | 400093 | 92 | 1
RegioLightControlFunction |  | Select light control function 0=Central controlled 1=Local Time controlled 2=Presence controlled 3=Time or Presence controlled 4=Central controlled or Presence controlled |  | X | 3 | 957 | HoldingRegister | 400071 | 70 | 1 |  | multi_state_value 1=Central controlled 2=Local Time controlled 3=Presence controlled 4=Time or Presence controlled 5=Central controlled or Presence controlled | 30031 |  | X
RegioLightManual |  | Controls the light when central control |  | L | 3 | 958 | Coil | 10 | 9 |  |  | binary_value | 10001 |  | X
RegioLightingCmdRemote |  | Remote Light Control |  | L | 3 | 959 | Coil | 11 | 10 |  |  | binary_value | 10002 |  | X
RegioLightControlFunctionZone2 |  | Select light control function Room2 0=Central controlled, 1=Local Time controlled 2=Presence controlled 3=Time or Presence controlled 4=Central controlled or Presence controlled | Ardo | X | 3 | 960 | HoldingRegister | 400141 | 140 | 1 |  | multi_state_value 1=Central controlled 2=Local Time controlled 3=Presence controlled 4=Time or Presence controlled 5=Central controlled or Presence controlled | 30060 |  | X
RegioLightManualZone2 |  | Controls the light when central control Room2 | Ardo | L | 3 | 961 | Coil | 22 | 21 |  |  | binary_value | 10003 |  | X
RegioLightingCmdRemoteZone2 |  | Remote Light Control Room2 | Ardo | L | 3 | 962 | Coil | 23 | 22 |  |  | binary_value | 10004 |  | X
RegioSunBlindsInCmd |  | Command to take in jalousie |  | L | 3 | 972 | Coil | 12 | 11
RegioSunBlindsOutCmd |  | Command to take out jalousie |  | L | 3 | 973 | Coil | 13 | 12
RegioSunBlindsRunTime | 240 | Run time for controlling the jalousie in/out (sec) |  | I | 3 | 974 | HoldingRegister | 400072 | 71 | 1
RegioSunBlindsControl |  | Remote Control for the jalousie 0=Go In 1-Stop 2-Go out |  | X | 3 | 976 | HoldingRegister | 400073 | 72 | 1 |  | multi_state_value 1=Go in 2=Stop 3=Go Out | 30032 |  | X
RegioSunBlindsInCmdZone2 |  | Command to take in jalousie Room2 | Ardo | L | 3 | 977 | Coil | 24 | 23
RegioSunBlindsOutCmdZone2 |  | Command to take out jalousie Room2 | Ardo | L | 3 | 978 | Coil | 25 | 24
RegioSunBlindsRunTimeZone2 | 240 | Run time for controlling the jalousie in/out (sec) Room2 | Ardo | I | 3 | 979 | HoldingRegister | 400142 | 141 | 1
RegioSunBlindsControlZone2 |  | Remote Control for the jalousie Room2 0=Go In 1=Stop 2=Go out | Ardo | X | 3 | 981 | HoldingRegister | 400143 | 142 | 1 |  | multi_state_value 1=Go in 2=Stop 3=Go Out | 30061 |  | X
RegioChangeOverSelect | 2 | Select Change Over 0=heating 1=cooling 2=Auto |  | X | 3 | 991 | HoldingRegister | 400035 | 34 | 1 |  | multi_state_value 1=Heating 2=Cooling 3=Auto | 30017 |  | X
RegioChangeOverType |  | Type of Changeover used in Room 1 0=Digital (Thermostat) 1=Analog Temperature in IncomingPipe |  | L | 3 | 992 | Coil | 4 | 3
RegioChangeOverAIDiffHeat | 3 | The difference between the temperature in the room and the media temperature for change over to cooling |  | R | 3 | 993 | HoldingRegister | 400036 | 35 | 1 |  | analog_value | 30018 | degrees_celsius | X
RegioChangeOverAIDiffCool | 4 | The difference between the temperature in the room and the media temperature for change over to heating |  | R | 3 | 996 | HoldingRegister | 400037 | 36 | 1 |  | analog_value | 30019 | degrees_celsius | X
RegioChangeOverValveTime | 600 | The minimum time the valve is opened during change over calculation |  | I | 3 | 999 | HoldingRegister | 400038 | 37 | 1
RegioRUType |  | Room Unit attached to the controller 0=None 1=ED-RU 2=ED-RU-O 3=ED-RU-F 4=ED-RU-FO 5=ED-RU-DO 6=ED-RU-DFO 7=ED-RU-DOS 8=ED-RU-H 9=ED-RU-DOCS 10=ED-RUD/ED-RUD-2 |  | X | 3 | 1010 | HoldingRegister | 400316 | 315 | 1
RegioRUTempUnit | 1 | Display Unit 0=None 1=°C 2=°F |  | X | 3 | 1013 | HoldingRegister | 400318 | 317 | 1 |  | multi_state_value 1=None 2=�C 3=�F | 30120 |  | X
RegioRUTemperatureComp |  | Temperature Compensation for RU 1 |  | R | 3 | 1014 | HoldingRegister | 400319 | 318 | 1
RegioRUUserELASelection |  | User ELA Selection for Room Unit 0=Auto Detect |  | X | 3 | 1017 | HoldingRegister | 400317 | 316 | 1
RegioRUDisplayViewType |  | Select view mode for the display 0=Display temperature value 1=Heat setpoint 2=Cool setpoint 3=Average cool/heat setpoint 4=Only setpoint offset 5=CO2 Level |  | X | 3 | 1018 | HoldingRegister | 400320 | 319 | 1
RegioRUDisplaySetPointType |  | Select view mode for the display when pressing increase decrease button 0=Setpoint offset 1=Controlling setpoint 2=Heat setpoint 3=Cool setpoint |  | X | 3 | 1020 | HoldingRegister | 400321 | 320 | 1
RegioRUSetPointAdjTimeOut | 5 | Time-out for setpoint adjustment (sec) |  | X | 3 | 1021 | HoldingRegister | 400322 | 321 | 1
RegioRUMenuTimeOut | 10 | Time-out for menu (sec) |  | X | 3 | 1022 | HoldingRegister | 400323 | 322 | 1
RegioRUOnOffButtonLongPressTime | 5 | Time (sec) that On/Off button must be pushed before Shutdown state |  | X | 3 | 1023 | HoldingRegister | 400324 | 323 | 1
RegioRUNoOfSelectMenus | 8 | Number of menus visible in the RU-DOS |  | X | 3 | 1024 | HoldingRegister | 400325 | 324 | 1
RegioRUNoOfDecimals | 1 | Number of decimal to be showed |  | X | 3 | 1025 | HoldingRegister | 400326 | 325 | 1
RegioRUDisplayBacklightTime |  | Time for backlight (sec) |  | I | 3 | 1026 | HoldingRegister | 400327 | 326 | 1
RegioRUButtonsUsed | 7 | Buttons that can be used in the RU |  | X | 3 | 1028 | HoldingRegister | 400328 | 327 | 1 |  | analog_value | 30121 | no_units | X
RegioRUConfigMenuDisable |  | Enable entering the configuration menu in the RU unit when pressing the UP and Down Key |  | L | 3 | 1029 | Coil | 49 | 48 |  |  | binary_value | 10005 |  | X
RegioUseRemoteValues | 1 | If 1 it will show in the RU the network avalues from the master controller(All controllers Average) if 0 will display its own room temperature |  | L | 3 | 1030 | Coil | 50 | 49
RegioRUDisplayBacklightLow | 20 | Lightning Lo (0-255) |  | X | 3 | 1035 | HoldingRegister | 400329 | 328 | 1
RegioRUDisplayBacklightHigh | 100 | Lightning Hi (0-255) |  | X | 3 | 1036 | HoldingRegister | 400330 | 329 | 1
RegioRUDisplayContrast | 15 | Contrast (0-15) |  | X | 3 | 1037 | HoldingRegister | 400331 | 330 | 1
RegioRUTypeZone2 |  | Room Unit attached to the controller Room2 0=None 1=ED-RU 2=ED-RU-O 3=ED-RU-F 4=ED-RU-FO 5=ED-RU-DO 6=ED-RU-DFO 7=ED-RU-DOS 8=ED-RU-H 9=ED-RU-DOCS 10=ED-RUD/ED-RUD-2 | Ardo | X | 3 | 1038 | HoldingRegister | 400332 | 331 | 1
RegioRUTempUnitZone2 | 1 | Display Unit Room2 0=None 1=°C 2=°F | Ardo | X | 3 | 1041 | HoldingRegister | 400336 | 335 | 1
RegioRUTemperatureCompZone2 |  | Temperature Compensation for RU Room2 | Ardo | R | 3 | 1042 | HoldingRegister | 400337 | 336 | 1 |  | analog_value | 30122 | degrees_celsius | X
RegioRUUserELASelectionZone2 |  | User ELA Selection for Room Unit in Room2 0=Auto Detect | Ardo | X | 3 | 1045 | HoldingRegister | 400333 | 332 | 1
RegioRUDisplayViewTypeZone2 |  | Select view mode for the display Room2 0=Display temperature value 1=Heat setpoint 2=Cool setpoint 3=Average cool/heat setpoint 4=Only setpoint offset 5=CO2 Level | Ardo | X | 3 | 1046 | HoldingRegister | 400338 | 337 | 1
RegioRUDisplaySetPointTypeZone2 |  | Select view mode for the display when pressing increase decrease button Room2 0=Setpoint offset 1=Controlling setpoint 2=Heat setpoint 3=Cool setpoint | Ardo | X | 3 | 1048 | HoldingRegister | 400339 | 338 | 1
RegioRUSetPointAdjTimeOutZone2 | 5 | Time-out for setpoint adjustment (sec), room 2 | Ardo | X | 3 | 1049 | HoldingRegister | 400340 | 339 | 1
RegioRUMenuTimeOutZone2 | 10 | Time-out for menu (sec), room 2 | Ardo | X | 3 | 1050 | HoldingRegister | 400341 | 340 | 1
RegioRUOnOffButtonLongPressTimeZone2 | 5 | Time (sec) that On/Off button must be pushed before Shutdown state, room 2 | Ardo | X | 3 | 1051 | HoldingRegister | 400342 | 341 | 1
RegioRUNoOfSelectMenusZone2 | 8 | Number of menus visible in the RU-DOS, room 2 | Ardo | X | 3 | 1052 | HoldingRegister | 400343 | 342 | 1
RegioRUNoOfDecimalsZone2 | 1 | Number of decimal to be showed, room 2 | Ardo | X | 3 | 1053 | HoldingRegister | 400344 | 343 | 1
RegioRUDisplayBacklightTimeZone2 |  | Time for backlight (sec), room 2 | Ardo | I | 3 | 1054 | HoldingRegister | 400345 | 344 | 1
RegioRUButtonsUsedZone2 | 7 | Buttons that can be used in the RU, room 2 | Ardo | X | 3 | 1056 | HoldingRegister | 400346 | 345 | 1 |  | analog_value | 30123 | no_units | X
RegioRUConfigMenuDisableZone2 |  | Enable entering the configuration menu in the RU unit, Room2, when pressing the Up and Down Key | Ardo | L | 3 | 1057 | Coil | 51 | 50 |  |  | binary_value | 10006 |  | X
RegioUseRemoteValuesZone2 | 1 | If 1 it will show in the RU, Room2, the network values from the master controller (All controllers Average). If 0 it will display its own room temperature | Ardo | L | 3 | 1058 | Coil | 52 | 51
RegioRUDisplayBacklightLowZone2 | 20 | Lightning Lo (0-255), room 2 | Ardo | X | 3 | 1063 | HoldingRegister | 400347 | 346 | 1
RegioRUDisplayBacklightHighZone2 | 100 | Lightning Hi (0-255), room 2 | Ardo | X | 3 | 1064 | HoldingRegister | 400348 | 347 | 1
RegioRUDisplayContrastZone2 | 15 | Contrast (0-15), room 2 | Ardo | X | 3 | 1065 | HoldingRegister | 400349 | 348 | 1
RegioAlarmHyst | 0.2 | Alarm hysteresis |  | R | 3 | 1127 | HoldingRegister | 400350 | 349 | 10 |  | analog_value | 30124 | no_units | X
RegioRoomTempHighLimit | 40 | High room temp |  | R | 3 | 1130 | HoldingRegister | 400351 | 350 | 1 |  | analog_value | 30125 | no_units | X
RegioRoomTempLowLimit | 15 | Low room temp |  | R | 3 | 1133 | HoldingRegister | 400352 | 351 | 1 |  | analog_value | 30126 | no_units | X
RegioRoomTempMaxDeviationLimit | 20 | Max allowed difference between setpoint and room temp before alarm |  | R | 3 | 1136 | HoldingRegister | 400353 | 352 | 1 |  | analog_value | 30127 | no_units | X
RegioAlarmHystZone2 | 0.2 | Alarm hysteresis Room2 | Ardo | R | 3 | 1140 | HoldingRegister | 400354 | 353 | 10 |  | analog_value | 30128 | no_units | X
RegioRoomTempHighLimitZone2 | 40 | High room temp Room2 | Ardo | R | 3 | 1143 | HoldingRegister | 400355 | 354 | 1 |  | analog_value | 30129 | no_units | X
RegioRoomTempLowLimitZone2 | 15 | Low room temp Room2 | Ardo | R | 3 | 1146 | HoldingRegister | 400356 | 355 | 1 |  | analog_value | 30130 | no_units | X
RegioRoomTempMaxDeviationLimitZone2 | 20 | Max allowed difference between setpoint and room temp before alarm Room2 | Ardo | R | 3 | 1149 | HoldingRegister | 400357 | 356 | 1 |  | analog_value | 30131 | no_units | X
RegioCO2MaxLimit | 1500 | Max CO2 Level for Alarm |  | R | 3 | 1152 | HoldingRegister | 400362 | 361 | 1 |  | analog_value | 30136 | parts_per_million | X
RegioCO2MaxLimitZone2 | 1500 | Max CO2 Level for Alarm Room2 | Ardo | R | 3 | 1155 | HoldingRegister | 400363 | 362 | 1 |  | analog_value | 30137 | parts_per_million | X
RegioCondenseLimit | 80 | High limit for condense alarm |  | R | 3 | 1167 | HoldingRegister | 400358 | 357 | 1 |  | analog_value | 30132 | no_units | X
RegioCondenseHyst | 2 | Condense alarm hysteresis |  | R | 3 | 1170 | HoldingRegister | 400359 | 358 | 1 |  | analog_value | 30133 | no_units | X
RegioDisable2ndSequence |  | If enabled when Condensation input is active in modes with 2 sequences the 2nd sequence will also be set to 0% |  | L | 3 | 1173 | Coil | 57 | 56
RegioCondenseLimitZone2 | 80 | High limit for condense alarm Room2 | Ardo | R | 3 | 1175 | HoldingRegister | 400360 | 359 | 1 |  | analog_value | 30134 | no_units | X
RegioCondenseHystZone2 | 2 | Condense alarm hysteresis Room2 | Ardo | R | 3 | 1178 | HoldingRegister | 400361 | 360 | 1 |  | analog_value | 30135 | no_units | X
RegioDisable2ndSequenceZone2 |  | If enabled when Condensation input is active in modes with 2 sequences the 2nd sequence will also be set to 0% Room2 | Ardo | L | 3 | 1181 | Coil | 58 | 57
RegioPort1Func | 2 | Defines the function for Port1 0=Not used 1=Exoline Master 2=Exoline Slave 3=Modbus Master 4=Modbus Slave 5=BACnet 6=Room Unit Display |  | X | 3 | 1192 | HoldingRegister | 400364 | 363 | 1
RegioPort2Func | 1 | Defines the function for Port2 0=Not used 1=Exoline Master 2=Exoline Slave 3=Modbus Master 4=Modbus Slave 5=BACnet 6=Room Unit Display |  | X | 3 | 1193 | HoldingRegister | 400369 | 368 | 1
RegioPort1Parity | 1 | Port 1 Parity 0=No Parity 1=Odd 2=Even |  | X | 3 | 1194 | HoldingRegister | 400366 | 365 | 1
RegioPort2Parity | 1 | Port 1 Parity 0=No Parity 1=Odd 2=Even |  | X | 3 | 1195 | HoldingRegister | 400371 | 370 | 1
RegioBaud_Port_1 |  | Bit rate Port 1 |  | X | 3 | 1196 | HoldingRegister | 400365 | 364 | 1
RegioTimeOut_Port_1 |  | Port 1 Time-out |  | X | 3 | 1197 | HoldingRegister | 400367 | 366 | 1
RegioCharTimeOut_Port_1 |  | Port 1 Char Time Out |  | I | 3 | 1198 | HoldingRegister | 400368 | 367 | 1
RegioBaud_Port_2 |  | Bit rate Port 2 |  | X | 3 | 1200 | HoldingRegister | 400370 | 369 | 1
RegioTimeOut_Port_2 |  | Port 2 Time-out |  | X | 3 | 1201 | HoldingRegister | 400372 | 371 | 1
RegioCharTimeOut_Port_2 |  | Port 2 Char Time Out |  | I | 3 | 1202 | HoldingRegister | 400373 | 372 | 1
RegioMasterPort |  | - |  | X | 3 | 1204 | HoldingRegister | 400374 | 373 | 1
RegioRouterDefaultRoute | 2 | - |  | X | 3 | 1205 | HoldingRegister | 400375 | 374 | 1
RegioMin_PLA |  | - |  | X | 3 | 1206 | HoldingRegister | 400376 | 375 | 1
RegioMax_PLA | 255 | - |  | X | 3 | 1207 | HoldingRegister | 400377 | 376 | 1
RegioMin_ELA |  | - |  | X | 3 | 1208 | HoldingRegister | 400378 | 377 | 1
RegioMax_ELA | 255 | - |  | X | 3 | 1209 | HoldingRegister | 400379 | 378 | 1
RegioTcpIpMasterAddrCommit | 1 | - |  | L | 3 | 1249 | Coil | 59 | 58
RegioTCPIPMasterAnswerTimeout | 25 | - |  | I | 3 | 1250 | HoldingRegister | 400380 | 379 | 1
RegioModbusIpEnable | 1 | Enables Modbus IP |  | L | 3 | 1269 | Coil | 60 | 59
RegioModbusSlaveAddr | 1 | Modbus slave address |  | X | 3 | 1270 | HoldingRegister | 400381 | 380 | 1
RegioBACnetIpEnable | 1 | Enables BACnet IP datalink |  | L | 3 | 1280 | Coil | 61 | 60
RegioRemovableWallsMaster |  | Set to 1 to enable master Multiple Controllers on Port Define on RemovableWallsCommPort |  | L | 3 | 1300 | Coil | 64 | 63
RegioRemovableWallsSlave |  | Set to 1 to enable slave Multiple Controllers on Port Define on RemovableWallsCommPort |  | L | 3 | 1301 | Coil | 65 | 64
RegioUseMasterValues |  | Set to 1 to enable Removable walls but only use the master sensors values to feed into the control loop |  | L | 3 | 1302 | Coil | 66 | 65
RegioRemovableWallsCommPort |  | Port used for multiple controllers |  | X | 3 | 1303 | HoldingRegister | 400383 | 382 | 1
RegioRemovableWallsNSlaves |  | Number of slaves in the Network Max 4 |  | X | 3 | 1304 | HoldingRegister | 400384 | 383 | 1
RegioRemovableWallsPLASlaves(0) |  | PLA Address Slaves |  | X | 3 | 1305 | HoldingRegister | 400385 | 384 | 1
RegioRemovableWallsPLASlave1 | 254 | PLA Slave 1 |  | X | 3 | 1306 | HoldingRegister | 400386 | 385 | 1
RegioRemovableWallsPLASlave2 | 254 | PLA Slave 2 |  | X | 3 | 1307 | HoldingRegister | 400387 | 386 | 1
RegioRemovableWallsPLASlave3 | 254 | PLA Slave 3 |  | X | 3 | 1308 | HoldingRegister | 400388 | 387 | 1
RegioRemovableWallsPLASlave4 | 254 | PLA Slave 4 |  | X | 3 | 1309 | HoldingRegister | 400389 | 388 | 1
RegioRemovableWallsELASlaves(0) |  | ELA Address Slaves |  | X | 3 | 1310 | HoldingRegister | 400390 | 389 | 1
RegioRemovableWallsELASlave1 | 31 | ELA Slave 1 |  | X | 3 | 1311 | HoldingRegister | 400391 | 390 | 1
RegioRemovableWallsELASlave2 | 32 | ELA Slave 2 |  | X | 3 | 1312 | HoldingRegister | 400392 | 391 | 1
RegioRemovableWallsELASlave3 | 33 | ELA Slave 3 |  | X | 3 | 1313 | HoldingRegister | 400393 | 392 | 1
RegioRemovableWallsELASlave4 | 34 | ELA Slave 4 |  | X | 3 | 1314 | HoldingRegister | 400394 | 393 | 1
RegioNRetries | 3 | Number of retries to read/write var from/to slaves |  | X | 3 | 1315 | HoldingRegister | 400395 | 394 | 1
RegioSlaveCommTimeOut | 3 | Minutes with missed communication from master to a slave consider that there is a comm failure and revert back to control it's own outputs |  | I | 3 | 1316 | HoldingRegister | 400396 | 395 | 1
RegioRemoteDIOpenWindow |  | Communication Open Window State |  | L | 3 | 1335 | Coil | 87 | 86
RegioRemoteDIPresence |  | Communication Presence State |  | L | 3 | 1336 | Coil | 88 | 87
RegioRemoteDIChangeover |  | Communication ChangeOver State |  | L | 3 | 1337 | Coil | 89 | 88
RegioRemoteDICondenseAlarm |  | Communication Condensation State |  | L | 3 | 1338 | Coil | 90 | 89
RegioRemoteDIOpenWindowZone2 |  | Communication Open Window Room2 State | Ardo | L | 3 | 1339 | Coil | 91 | 90
RegioRemoteDIPresenceZone2 |  | Communication Presence Room2 State | Ardo | L | 3 | 1340 | Coil | 92 | 91
RegioRemoteDICondenseAlarmZone2 |  | Communication Condensation Room2 State | Ardo | L | 3 | 1341 | Coil | 93 | 92
RegioRemoteDIOpenWindowSelect |  | Open Window Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1342 | Coil | 80 | 79
RegioRemoteDIPresenceSelect |  | Presence Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1343 | Coil | 81 | 80
RegioRemoteDIChangeoverSelect |  | ChangeOver State Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1344 | Coil | 82 | 81
RegioRemoteDICondenseAlarmSelect |  | Condensation State Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1345 | Coil | 83 | 82
RegioRemoteDIOpenWindowZone2Select |  | Open Window Room2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1346 | Coil | 84 | 83
RegioRemoteDIPresenceZone2Select |  | Presence Room2 Source Selector 0=Use Controller Input Values 1=Use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1347 | Coil | 85 | 84
RegioRemoteDICondenseAlarmZone2Select |  | Condensation Room2 State Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1348 | Coil | 86 | 85
RegioRemoteRoomTemp |  | Communication Room Temperature Value |  | R | 3 | 1349 | HoldingRegister | 400397 | 396 | 10
RegioRemoteAIChangeOver |  | Communication Changeover Temperature Value |  | R | 3 | 1352 | HoldingRegister | 400398 | 397 | 10
RegioRemoteOutDoorTemp |  | Communication Outdoor Temperature Value |  | R | 3 | 1355 | HoldingRegister | 400399 | 398 | 10
RegioRemoteCondense |  | Communication Condensation Value |  | R | 3 | 1358 | HoldingRegister | 400400 | 399 | 1
RegioRemoteRoomCO2 |  | Communication CO2 Value |  | R | 3 | 1361 | HoldingRegister | 400401 | 400 | 1
RegioRemoteRoomRH |  | Communication RH Value |  | R | 3 | 1364 | HoldingRegister | 400402 | 401 | 1
RegioRemoteSupplyAir |  | Communication Supply Air Temperature Value |  | R | 3 | 1367 | HoldingRegister | 400403 | 402 | 10
RegioRemoteRoomTempZone2 |  | Communication Room Temperature Room2 Value | Ardo | R | 3 | 1370 | HoldingRegister | 400404 | 403 | 10
RegioRemoteOutDoorTempZone2 |  | Communication Outdoor Temperature Room2 Value | Ardo | R | 3 | 1373 | HoldingRegister | 400405 | 404 | 10
RegioRemoteCondenseZone2 |  | Communication Condensation Room2 Value | Ardo | R | 3 | 1376 | HoldingRegister | 400406 | 405 | 1
RegioRemoteRoomCO2Zone2 |  | Communication CO2 Room2 Value | Ardo | R | 3 | 1380 | HoldingRegister | 400407 | 406 | 1
RegioRemoteRoomRHZone2 |  | Communication RH Room2 Value | Ardo | R | 3 | 1383 | HoldingRegister | 400408 | 407 | 1
RegioRemoteSupplyAirTempZone2 |  | Communication Supply Air Temperature Room2 Value | Ardo | R | 3 | 1386 | HoldingRegister | 400409 | 408 | 10
RegioRemoteUnderfloortemp |  | Communication Underfloor Temperature Value |  | R | 3 | 1389 | HoldingRegister | 400476 | 475 | 10 |  | analog_value | 30202 | degrees_celsius | X
RegioRemoteUnderfloortempZone2 |  | Communication Underfloor Temperature Value Room2 | Ardo | R | 3 | 1392 | HoldingRegister | 400485 | 484 | 10 |  | analog_value | 30211 | degrees_celsius | X
RegioRemoteRoomTempSelect |  | Room Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1395 | Coil | 67 | 66
RegioRemoteAIChangeOverSelect |  | ChangeOver Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1396 | Coil | 68 | 67
RegioRemoteOutDoorTempSelect |  | Outdoor Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1397 | Coil | 69 | 68
RegioRemoteCondenseSelect |  | Condensation Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1398 | Coil | 70 | 69
RegioRemoteRoomCO2Select |  | CO2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1399 | Coil | 71 | 70
RegioRemoteRoomRHSelect |  | RH Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1400 | Coil | 72 | 71
RegioRemoteSupplyAirSelect |  | Supply Air Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1401 | Coil | 73 | 72
RegioRemoteRoomTempZone2Select |  | Room Temperature Room2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1402 | Coil | 74 | 73
RegioRemoteOutDoorTempZone2Select |  | Outdoor Temperature Room2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1403 | Coil | 75 | 74
RegioRemoteCondenseZone2Select |  | Condensation Room2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1404 | Coil | 76 | 75
RegioRemoteRoomCO2Zone2Select |  | CO2 Room2 Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1405 | Coil | 77 | 76
RegioRemoteRoomRHZone2Select |  | RH Room2 Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1406 | Coil | 78 | 77
RegioRemoteSupplyAirTempZone2Select |  | Supply Air Room2 Temperature Source Selector 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1407 | Coil | 79 | 78
RegioRemoteUnderfloorTempSelect |  | Underfloor heating temperature source selector 0= Use controller input values 1= Use remote values (Exoline/Modbus/BACnet) |  | L | 3 | 1408 | Coil | 97 | 96 |  |  | binary_value | 10012 |  | X
RegioRemoteUnderfloorTempSelectZone2 |  | Underfloor Temperature Source Selector 0-Use Controller Input Values 1-use remote values (Exoline/Modbus/BACnet) | Ardo | L | 3 | 1409 | Coil | 100 | 99 |  |  | binary_value | 10015 |  | X
RegioLogActive | 1 | Activate log function for EXOScada |  | L | 3 | 1443 | Coil | 62 | 61
RegioAlarmActive | 3 | Activate alarm and events function for EXOScada 0=Not active 1=Only alarm 2=Only events 3=Alarm and events is active |  | X | 3 | 1444 | HoldingRegister | 400382 | 381 | 1
RegioAutoSummerTime | 1 | Switch automatically between summer and winter time |  | L | 3 | 1445 | Coil | 63 | 62 |  |  | binary_value | 10008 |  | X
RegioForceDisplayID |  | Forces the Display to identify themselves(show number on display/blink leds), can leave this state by pressing On/Off button | Ardo | L | 3 | 1446 | Coil | 53 | 52 |  |  | binary_value | 10007 |  | X
RegioDisplayIDOnPowerUp |  | If enabled will show display identification on power for 60 seconds or press of the on/off button | Ardo | L | 3 | 1447 | Coil | 54 | 53
RegioForceDisplaySearch |  | Trigger a search for display on display port | Ardo | L | 3 | 1448 | Coil | 55 | 54
RegioSwapDisplayAddress |  | Swap the address of the display. RU in Room1 will go to Room2 and vice versa. Only possible with two display detected and Dual Zone Active | Ardo | L | 3 | 1449 | Coil | 56 | 55
RegioEnableCommFailsafe |  | Enables/Disables the communication Failsafe function 0= Disable 1= Enable |  | L | 3 | 1450 | Coil | 95 | 94 |  |  | binary_value | 10010 |  | X
RegioFailsafetime | 10 | Communication failure safe time for triggering Failsafe |  | X | 3 | 1451 | HoldingRegister | 400455 | 454 | 1 |  | analog_value | 30181 | minutes | X
RegioFailsafeState |  | State the controller will revert to if communication Failsafe is active 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 4=Bypass 5=Keep Current |  | X | 3 | 1452 | HoldingRegister | 400456 | 455 | 1 |  | multi_state_value 1=Off 2=Unoccupied 3=Stand-by 4=Occupied 5=ByPass 6=Resume Normal Operation | 30182 |  | X
RegioVAVOutputMinLimitBypass | 20 | Min Limit for VAV Output at Bypass State |  | R | 3 | 1453 | HoldingRegister | 400470 | 469 | 1 |  | analog_value | 30196 | percent | X
RegioVAVOutputMinLimitBypassZone2 | 20 | Min Limit for VAV Output at Bypass State for Zone 2 | Ardo | R | 3 | 1456 | HoldingRegister | 400471 | 470 | 1 |  | analog_value | 30197 | percent | X
RegioAnalog1Select | 2 | Manual Selection for Analog Output 1 0=Off 1=Manual 2=Auto |  | X | 3 | 1459 | HoldingRegister | 400457 | 456 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30183 |  | X
RegioAnalog2Select | 2 | Manual Selection for Analog Output 2 |  | X | 3 | 1460 | HoldingRegister | 400458 | 457 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30184 |  | X
RegioAnalog3Select | 2 | Manual Selection for Analog Output 3 |  | X | 3 | 1461 | HoldingRegister | 400459 | 458 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30185 |  | X
RegioAnalog4Select | 2 | Manual Selection for Analog Output 4 |  | X | 3 | 1462 | HoldingRegister | 400460 | 459 | 1 |  | multi_state_value 1=Off 2=Manual 3=Auto | 30186 |  | X
RegioAnalog1ManualValue |  | Analog Manual Value for Analog Output 1 |  | R | 3 | 1469 | HoldingRegister | 400461 | 460 | 10 |  | analog_value | 30187 | volts | X
RegioAnalog2ManualValue |  | Analog Manual Value for Analog Output 2 |  | R | 3 | 1472 | HoldingRegister | 400462 | 461 | 10 |  | analog_value | 30188 | volts | X
RegioAnalog3ManualValue |  | Analog Manual Value for Analog Output 3 |  | R | 3 | 1475 | HoldingRegister | 400463 | 462 | 10 |  | analog_value | 30189 | volts | X
RegioAnalog4ManualValue |  | Analog Manual Value for Analog Output 4 |  | R | 3 | 1478 | HoldingRegister | 400464 | 463 | 10 |  | analog_value | 30190 | volts | X
RegioDigital1Select | 2 | Manual Selection for Digital Output 1 0=Off 1=On 2=Auto |  | X | 3 | 1499 | HoldingRegister | 400465 | 464 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30191 |  | X
RegioDigital2Select | 2 | Manual Selection for Digital Output 2 |  | X | 3 | 1500 | HoldingRegister | 400466 | 465 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30192 |  | X
RegioDigital3Select | 2 | Manual Selection for Digital Output 3 |  | X | 3 | 1501 | HoldingRegister | 400467 | 466 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30193 |  | X
RegioDigital4Select | 2 | Manual Selection for Digital Output 4 |  | X | 3 | 1502 | HoldingRegister | 400468 | 467 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30194 |  | X
RegioDigital5Select | 2 | Manual Selection for Digital Output 5 |  | X | 3 | 1503 | HoldingRegister | 400469 | 468 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30195 |  | X
RegioDigital6Select | 2 | Manual Selection for Digital Output 6 0=Off 1=On 2=Auto | Ardo | X | 3 | 1504 | HoldingRegister | 400504 | 503 | 1 |  | multi_state_value 1=Off 2=On 3=Auto | 30196 |  | X
RegioUnderfloorHeatingSetpoint | 22 | Room Setpoint for underfloor heating |  | R | 3 | 1514 | HoldingRegister | 400472 | 471 | 10 |  | analog_value | 30198 | degrees_celsius | X
RegioUnderfloorHeatingEnable |  | Underfloor Enable Condition |  | X | 3 | 1517 | HoldingRegister | 400473 | 472 | 1 |  | multi_state_value 1=Disabled 2=Higher than off 3=Higher than Unocc 4=Higher than Stanby 5=Higher than Occ 6=Always on | 30199 |  | X
RegioUnderfloorHeatingPBand | 10 | Underfloor heating PI Control P Band |  | R | 3 | 1518 | HoldingRegister | 400474 | 473 | 1 |  | analog_value | 30200 | no_units | X
RegioUnderfloorHeatingITime | 300 | Underfloor heating PI Control I Time |  | R | 3 | 1521 | HoldingRegister | 400475 | 474 | 1 |  | analog_value | 30201 | seconds | X
RegioUnderfloorHeatingDisableCooling | 1 | Disable underfloor heating when main aera is cooling |  | L | 3 | 1524 | Coil | 96 | 95 |  |  | binary_value | 10011 |  | X
RegioUnderfloorHeatingSetpointZone2 | 22 | Room Setpoint for underfloor heating | Ardo | R | 3 | 1525 | HoldingRegister | 400481 | 480 | 10 |  | analog_value | 30207 | degrees_celsius | X
RegioUnderfloorHeatingEnableZone2 |  | Underfloor Enable Condition | Ardo | X | 3 | 1528 | HoldingRegister | 400482 | 481 | 1 |  | multi_state_value 1=Disabled 2=Higher than off 3=Higher than Unocc 4=Higher than Stanby 5=Higher than Occ 6=Always on | 30208 |  | X
RegioUnderfloorHeatingPBandZone2 | 10 | Underfloor heating PI Control P Band | Ardo | R | 3 | 1529 | HoldingRegister | 400483 | 482 | 1 |  | analog_value | 30209 | no_units | X
RegioUnderfloorHeatingITimeZone2 | 300 | Underfloor heating PI Control I Time Room2 | Ardo | R | 3 | 1532 | HoldingRegister | 400484 | 483 | 1 |  | analog_value | 30210 | seconds | X
RegioUnderfloorHeatingDisableCoolingZone2 | 1 | Disable underfloor heating when main aera is cooling | Ardo | L | 3 | 1535 | Coil | 99 | 98 |  |  | binary_value | 10014 |  | X
RegioResetRUSettingsOnShutdow |  | Enables reset of user inputs on shutdown 0= Disable 1= Enable |  | L | 3 | 1536 | Coil | 102 | 101 |  |  | binary_value | 10017 |  | X
RegioResetRUSettingsOnShutdowZone2 |  | Enables reset of user inputs on shutdown for zone 2 | Ardo | L | 3 | 1537 | Coil | 103 | 102 |  |  | binary_value | 10018 |  | X
RegioECFanAtForcedVentilation |  | EC Fan speed at forced ventilation |  | R | 3 | 1538 | HoldingRegister | 400490 | 489 | 1 |  | analog_value | 30216 | percent | X
RegioECFanAtForcedVentilationZone2 |  | EC Fan speed at forced ventilation for zone 2 | Ardo | R | 3 | 1541 | HoldingRegister | 400491 | 490 | 1 |  | analog_value | 30217 | percent | X
RegioFanButtonBehaviour |  | Fan Button Behavior 0=Manual fan control (default setting) 1=Activates forced ventilation |  | L | 3 | 1544 | Coil | 104 | 103 |  |  | binary_value | 10019 |  | X
RegioFanButtonBehaviourZone2 |  | Fan Button Behavior Room2 0=Manual fan control (default setting) 1=Activates forced ventilation | Ardo | L | 3 | 1545 | Coil | 105 | 104 |  |  | binary_value | 10020 |  | X
RegioRoomtemp_0V |  | Room temperature at 0 Volt input |  | R | 3 | 1553 | HoldingRegister | 400492 | 491 | 1
RegioRoomtemp_10V | 100 | Room temperature at 10 Volt input |  | R | 3 | 1556 | HoldingRegister | 400493 | 492 | 1
RegioFlow_0V |  | Air flow at 0 Volt input |  | R | 3 | 1560 | HoldingRegister | 400494 | 493 | 1
RegioFlow_10V | 100 | Air flow at 10 Volt input |  | R | 3 | 1563 | HoldingRegister | 400495 | 494 | 1
RegioRoomtempFilterFactor | 0.2 | Filter factor for room temperature on analog input 0=no filter 1=Max filter |  | R | 3 | 1566 | HoldingRegister | 400496 | 495 | 100
RegioFlowFilterFactor | 0.2 | Filter factor for air flow on analog input 0=no filter 1=Max filter |  | R | 3 | 1569 | HoldingRegister | 400497 | 496 | 100
RegioRoomtemp_0VZone2 |  | Room temperature at 0 Volt input Room 2 | Ardo | R | 3 | 1572 | HoldingRegister | 400498 | 497 | 1
RegioRoomtemp_10VZone2 | 100 | Room temperature at 10 Volt input Room 2 | Ardo | R | 3 | 1575 | HoldingRegister | 400499 | 498 | 1
RegioFlow_0VZone2 |  | Air flow at 0 Volt input Room 2 | Ardo | R | 3 | 1578 | HoldingRegister | 400500 | 499 | 1
RegioFlow_10VZone2 | 100 | Air flow at 10 Volt input Room 2 | Ardo | R | 3 | 1581 | HoldingRegister | 400501 | 500 | 1
RegioRoomtempFilterFactorZone2 | 0.2 | Filter factor for room temperature on analog input Room 2 0=no filter 1=Max filter | Ardo | R | 3 | 1584 | HoldingRegister | 400502 | 501 | 100
RegioFlowFilterFactorZone2 | 0.2 | Filter factor for air flow on analog input Room 2 0=no filter 1=Max filter | Ardo | R | 3 | 1587 | HoldingRegister | 400503 | 502 | 100
RegioOutput1RU1 |  |  |  | I | 3 | 1590 | HoldingRegister | 400506 | 505
RegioOutput2RU1 |  |  |  | I | 3 | 1592 | HoldingRegister | 400507 | 506
RegioOutput3RU1 |  |  |  | I | 3 | 1594 | HoldingRegister | 400508 | 507
RegioOutput1RU2 |  |  | Ardo | I | 3 | 1602 | HoldingRegister | 400509 | 508
RegioOutput2RU2 |  |  | Ardo | I | 3 | 1604 | HoldingRegister | 400510 | 509
RegioOutput3RU2 |  |  | Ardo | I | 3 | 1606 | HoldingRegister | 400511 | 510
AlaAcknow | 255 | External acknowledge command |  | X | 37 | 1 | HoldingRegister | 400446 | 445 | 1 |  | analog_value | 30172 | no_units | X
AlaBlock | 255 | External blocking command |  | X | 37 | 2 | HoldingRegister | 400447 | 446 | 1 |  | analog_value | 30173 | no_units | X
AlaUnBlock | 255 | External unblocking command |  | X | 37 | 3 | HoldingRegister | 400448 | 447 | 1 |  | analog_value | 30174 | no_units | X
AlaPt1_Status |  | Status for point no. 1 Presence 0=Not used 1=Normal 2=Blocked 3=Acknowledge 4=Not used 5=Cancelled 6=Not used 7=Alarm |  | X | 39 | 1 | InputRegister | 300074 | 73 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40075
AlaPt2_Status |  | Status for point no. 2 OpenWindow |  | X | 39 | 2 | InputRegister | 300075 | 74 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40076
AlaPt3_Status |  | Status for point no. 3 Condensation |  | X | 39 | 3 | InputRegister | 300076 | 75 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40077
AlaPt4_Status |  | Status for point no. 4 RoomTempHigh |  | X | 39 | 4 | InputRegister | 300077 | 76 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40078
AlaPt5_Status |  | Status for point no. 5 RoomTempLow |  | X | 39 | 5 | InputRegister | 300078 | 77 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40079
AlaPt6_Status |  | Status for point no. 6 RoomTempDeviation |  | X | 39 | 6 | InputRegister | 300079 | 78 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40080
AlaPt7_Status |  | Status for point no. 7 RoomControllerInManualMode |  | X | 39 | 7 | InputRegister | 300080 | 79 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40081
AlaPt8_Status |  | Status for point no. 8 SensorAlarm |  | X | 39 | 8 | InputRegister | 300081 | 80 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40082
AlaPt9_Status |  | Status for point no. 9 RoomUnitError |  | X | 39 | 9 | InputRegister | 300082 | 81 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40083
AlaPt10_Status |  | Status for point no. 10 PresenceZone2 | Ardo | X | 39 | 10 | InputRegister | 300083 | 82 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40084
AlaPt11_Status |  | Status for point no. 11 OpenWindowsZone2 | Ardo | X | 39 | 11 | InputRegister | 300084 | 83 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40085
AlaPt12_Status |  | Status for point no. 12 CondensationZone2 | Ardo | X | 39 | 12 | InputRegister | 300085 | 84 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40086
AlaPt13_Status |  | Status for point no. 13 RoomTempHighZone2 | Ardo | X | 39 | 13 | InputRegister | 300086 | 85 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40087
AlaPt14_Status |  | Status for point no. 14 RoomTempLowZone2 | Ardo | X | 39 | 14 | InputRegister | 300087 | 86 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40088
AlaPt15_Status |  | Status for point no. 15 RoomTempDeviationZone2 | Ardo | X | 39 | 15 | InputRegister | 300088 | 87 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40089
AlaPt16_Status |  | Status for point no. 16 RoomControllerInManualModeZone2 | Ardo | X | 39 | 16 | InputRegister | 300089 | 88 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40090
AlaPt17_Status |  | Status for point no. 17 SensorAlarmZone2 | Ardo | X | 39 | 17 | InputRegister | 300090 | 89 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40091
AlaPt18_Status |  | Status for point no. 18 RoomUnitErrorZone2 | Ardo | X | 39 | 18 | InputRegister | 300091 | 90 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40092
AlaPt19_Status |  | Status for point no. 19 Slave1CommFail |  | X | 39 | 19 | InputRegister | 300092 | 91 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40093
AlaPt20_Status |  | Status for point no. 20 Slave2CommFail |  | X | 39 | 20 | InputRegister | 300093 | 92 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40094
AlaPt21_Status |  | Status for point no. 21 Slave3CommFail |  | X | 39 | 21 | InputRegister | 300094 | 93 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40095
AlaPt22_Status |  | Status for point no. 22 Slave4CommFail |  | X | 39 | 22 | InputRegister | 300095 | 94 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40096
AlaPt23_Status |  | Status for point no. 23 MasterCommFail |  | X | 39 | 23 | InputRegister | 300096 | 95 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40097
AlaPt24_Status |  | Status for point no. 24 SlaveNormalOperation |  | X | 39 | 24 | InputRegister | 300097 | 96 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40098
AlaPt25_Status |  | Status for point no. 25 CO2 Level High |  | X | 39 | 25 | InputRegister | 300098 | 97 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40099
AlaPt26_Status |  | Status for point no. 26 CO2 Level High Zone2 | Ardo | X | 39 | 26 | InputRegister | 300099 | 98 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40100
AlaPt27_Status |  | Status for point no. 27 Communication fail safe |  | X | 39 | 27 | InputRegister | 300100 | 99 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40101
AlaPt28_Status |  | Status for point no. 28 Hardware Manual Operation |  | X | 39 | 28 | InputRegister | 300101 | 100 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40102
AlaPt29_Status |  | Status for point no. 29 External Alarm Digital input 1 |  | X | 39 | 29 | InputRegister | 300102 | 101 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40103
AlaPt30_Status |  | Status for point no. 30 External Alarm Digital input 2 |  | X | 39 | 30 | InputRegister | 300103 | 102 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40104
AlaPt31_Status |  | Status for point no. 31 External Alarm Digital input 3 |  | X | 39 | 31 | InputRegister | 300104 | 103 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40105
AlaPt32_Status |  | Status for point no. 32 External Alarm Digital input 4 | Ardo | X | 39 | 32 | InputRegister | 300105 | 104 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40106
AlaPt33_Status |  | Status for point no. 33 Battery Failure |  | X | 39 | 33 | InputRegister | 300114 | 113 | 1 |  | multi_state_value 1=Not used 2=Normal 3=Blocked 4=Acknowledge 5=Not used 6=Cancelled 7=Not used 8=Alarm | 40107
AlaPt1_DelayValue |  | Delay value for point no. 1 Presence 0=Not used 1=Normal 2=Blocked 3=Acknowledge 4=Not used 5=Cancelled 6=Not used 7=Alarm |  | I | 39 | 70 | HoldingRegister | 400420 | 419 | 1 |  | analog_value | 30146 | no_units | X
AlaPt2_DelayValue |  | Delay value for point no. 2 OpenWindow |  | I | 39 | 72 | HoldingRegister | 400421 | 420 | 1 |  | analog_value | 30147 | no_units | X
AlaPt3_DelayValue |  | Delay value for point no. 3 Condensation |  | I | 39 | 74 | HoldingRegister | 400422 | 421 | 1 |  | analog_value | 30148 | no_units | X
AlaPt4_DelayValue |  | Delay value for point no. 4 RoomTempHigh |  | I | 39 | 76 | HoldingRegister | 400423 | 422 | 1 |  | analog_value | 30149 | no_units | X
AlaPt5_DelayValue |  | Delay value for point no. 5 RoomTempLow |  | I | 39 | 78 | HoldingRegister | 400424 | 423 | 1 |  | analog_value | 30150 | no_units | X
AlaPt6_DelayValue |  | Delay value for point no. 6 RoomTempDeviation |  | I | 39 | 80 | HoldingRegister | 400425 | 424 | 1 |  | analog_value | 30151 | no_units | X
AlaPt7_DelayValue |  | Delay value for point no. 7 RoomControllerInManualMode |  | I | 39 | 82 | HoldingRegister | 400426 | 425 | 1 |  | analog_value | 30152 | no_units | X
AlaPt8_DelayValue |  | Delay value for point no. 8 SensorAlarm |  | I | 39 | 84 | HoldingRegister | 400427 | 426 | 1 |  | analog_value | 30153 | no_units | X
AlaPt9_DelayValue |  | Delay value for point no. 9 RoomUnitError |  | I | 39 | 86 | HoldingRegister | 400428 | 427 | 1 |  | analog_value | 30154 | no_units | X
AlaPt10_DelayValue |  | Delay value for point no. 10 PresenceZone2 | Ardo | I | 39 | 88 | HoldingRegister | 400429 | 428 | 1 |  | analog_value | 30155 | no_units | X
AlaPt11_DelayValue |  | Delay value for point no. 11 OpenWindowsZone2 | Ardo | I | 39 | 90 | HoldingRegister | 400430 | 429 | 1 |  | analog_value | 30156 | no_units | X
AlaPt12_DelayValue |  | Delay value for point no. 12 CondensationZone2 | Ardo | I | 39 | 92 | HoldingRegister | 400431 | 430 | 1 |  | analog_value | 30157 | no_units | X
AlaPt13_DelayValue |  | Delay value for point no. 13 RoomTempHighZone2 | Ardo | I | 39 | 94 | HoldingRegister | 400432 | 431 | 1 |  | analog_value | 30158 | no_units | X
AlaPt14_DelayValue |  | Delay value for point no. 14 RoomTempLowZone2 | Ardo | I | 39 | 96 | HoldingRegister | 400433 | 432 | 1 |  | analog_value | 30159 | no_units | X
AlaPt15_DelayValue |  | Delay value for point no. 15 RoomTempDeviationZone2 | Ardo | I | 39 | 98 | HoldingRegister | 400434 | 433 | 1 |  | analog_value | 30160 | no_units | X
AlaPt16_DelayValue |  | Delay value for point no. 16 RoomControllerInManualModeZone2 | Ardo | I | 39 | 100 | HoldingRegister | 400435 | 434 | 1 |  | analog_value | 30161 | no_units | X
AlaPt17_DelayValue |  | Delay value for point no. 17 SensorAlarmZone2 | Ardo | I | 39 | 102 | HoldingRegister | 400436 | 435 | 1 |  | analog_value | 30162 | no_units | X
AlaPt18_DelayValue |  | Delay value for point no. 18 RoomUnitErrorZone2 | Ardo | I | 39 | 104 | HoldingRegister | 400437 | 436 | 1 |  | analog_value | 30163 | no_units | X
AlaPt19_DelayValue |  | Delay value for point no. 19 Slave1CommFail |  | I | 39 | 106 | HoldingRegister | 400438 | 437 | 1 |  | analog_value | 30164 | no_units | X
AlaPt20_DelayValue |  | Delay value for point no. 20 Slave2CommFail |  | I | 39 | 108 | HoldingRegister | 400439 | 438 | 1 |  | analog_value | 30165 | no_units | X
AlaPt21_DelayValue |  | Delay value for point no. 21 Slave3CommFail |  | I | 39 | 110 | HoldingRegister | 400440 | 439 | 1 |  | analog_value | 30166 | no_units | X
AlaPt22_DelayValue |  | Delay value for point no. 22 Slave4CommFail |  | I | 39 | 112 | HoldingRegister | 400441 | 440 | 1 |  | analog_value | 30167 | no_units | X
AlaPt23_DelayValue |  | Delay value for point no. 23 MasterCommFail |  | I | 39 | 114 | HoldingRegister | 400442 | 441 | 1 |  | analog_value | 30168 | no_units | X
AlaPt24_DelayValue |  | Delay value for point no. 24 SlaveNormalOperation |  | I | 39 | 116 | HoldingRegister | 400443 | 442 | 1 |  | analog_value | 30169 | no_units | X
AlaPt25_DelayValue | 10 | Delay value for point no. 25 CO2 Level High |  | I | 39 | 118 | HoldingRegister | 400444 | 443 | 1 |  | analog_value | 30170 | no_units | X
AlaPt26_DelayValue | 10 | Delay value for point no. 26 CO2 Level High Zone2 | Ardo | I | 39 | 120 | HoldingRegister | 400445 | 444 | 1 |  | analog_value | 30171 | no_units | X
AlaPt27_DelayValue |  | Delay value for point no. 27 Communication fail safe |  | I | 39 | 122 | HoldingRegister | 400449 | 448 | 1 |  | analog_value | 30175 | no_units | X
AlaPt28_DelayValue |  | Delay value for point no. 28 Hardware Manual Operation |  | I | 39 | 124 | HoldingRegister | 400450 | 449 | 1 |  | analog_value | 30176 | no_units | X
AlaPt29_DelayValue |  | Delay value for point no. 29 External Alarm Digital Input 1 |  | I | 39 | 126 | HoldingRegister | 400451 | 450 | 1 |  | analog_value | 30177 | no_units | X
AlaPt30_DelayValue |  | Delay value for point no. 30 External Alarm Digital Input 2 |  | I | 39 | 128 | HoldingRegister | 400452 | 451 | 1 |  | analog_value | 30178 | no_units | X
AlaPt31_DelayValue |  | Delay value for point no. 31 External Alarm Digital Input 3 |  | I | 39 | 130 | HoldingRegister | 400453 | 452 | 1 |  | analog_value | 30179 | no_units | X
AlaPt32_DelayValue |  | Delay value for point no. 32 External Alarm Digital Input 4 | Ardo | I | 39 | 132 | HoldingRegister | 400454 | 453 | 1 |  | analog_value | 30180 | no_units | X
AlaPt33_DelayValue |  | Delay value for point no. 33 Battery Failure |  | I | 39 | 134 | HoldingRegister | 400505 | 504 | 1 |  | analog_value | 30182 | no_units | X
PLA | 254 | Controller PLA Address |  | X | 241 | 0 | HoldingRegister | 400418 | 417 | 1
ELA | 30 | Controller ELA Address |  | X | 241 | 1 | HoldingRegister | 400419 | 418 | 1
Sec |  | System Time Seconds |  | X | 241 | 4 | HoldingRegister | 400410 | 409 | 1 |  | analog_value | 30138 | seconds | X
Minute |  | System Time Minutes |  | X | 241 | 5 | HoldingRegister | 400411 | 410 | 1 |  | analog_value | 30139 | minutes | X
Hour |  | System Time Hours |  | X | 241 | 6 | HoldingRegister | 400412 | 411 | 1 |  | analog_value | 30140 | hours | X
WDay |  | System WeekDay |  | X | 241 | 7 | HoldingRegister | 400413 | 412 | 1 |  | analog_value | 30141 | no_units | X
Week |  | System Week |  | X | 241 | 8 | HoldingRegister | 400414 | 413 | 1 |  | analog_value | 30142 | no_units | X
Date |  | System Date Day |  | X | 241 | 9 | HoldingRegister | 400415 | 414 | 1 |  | analog_value | 30143 | no_units | X
Month |  | System Date Month |  | X | 241 | 10 | HoldingRegister | 400416 | 415 | 1 |  | analog_value | 30144 | no_units | X
Year |  | System Date Year |  | X | 241 | 11 | HoldingRegister | 400417 | 416 | 1 |  | analog_value | 30145 | no_units | X