## Variables
Regio Eedo 2.1-1-00 - Variable list | [13 empty] | Revision: | A
|  |  | EXOline |  |  | Modbus |  |  |  |  | BACnet
Name | Default | Description | Type | Load | Cell | Register type | Register | Address | Scale | Offset | Object type | Instance | Unit | Writeable | Variable type
RegioSoftware |  | Type of Regio software (0=RPC) | X | 2 | 0 | InputRegister | 300002 | 1 | 1 |  | analog_value | 40003 | no_units
RegioVerMajor | 2 | Major Version | X | 2 | 1 | InputRegister | 300003 | 2 | 1 |  | analog_value | 40004 | no_units
RegioVerMinor | 1 | Minor Version | X | 2 | 2 | InputRegister | 300004 | 3 | 1 |  | analog_value | 40005 | no_units
RegioVerBranch | 1 | Branch Version (0=Beta, 1=Official) | X | 2 | 3 | InputRegister | 300005 | 4 | 1 |  | analog_value | 40006 | no_units
RegioRevision |  | Revision | X | 2 | 4 | InputRegister | 300006 | 5 | 1 |  | analog_value | 40007 | no_units
RegioRoomTempExt |  | Room temp external sensor | R | 2 | 66 | InputRegister | 300007 | 6 | 10 |  | analog_value | 40008 | degrees_celsius
RegioAIChangeOverTemp |  | Change over | R | 2 | 69 | InputRegister | 300008 | 7 | 10 |  | analog_value | 40009 | degrees_celsius
RegioOutdoorTemp |  | Outdoor temp | R | 2 | 72 | InputRegister | 300009 | 8 | 10 |  | analog_value | 40010 | degrees_celsius
RegioCondensation |  | Condense | R | 2 | 75 | InputRegister | 300010 | 9 | 1 |  | analog_value | 40011 | no_units
RegioRoomCO2 |  | Room CO2 | R | 2 | 78 | InputRegister | 300011 | 10 | 1 |  | analog_value | 40012 | parts_per_million
RegioRoomRH |  | Room RH | R | 2 | 81 | InputRegister | 300012 | 11 | 1 |  | analog_value | 40013 | percent_relative_humidity
RegioSupplyAirTemp |  | Supply Air Temperature | R | 2 | 84 | InputRegister | 300013 | 12 | 10 |  | analog_value | 40014 | degrees_celsius
RegioUnderfloorTemp |  | Underfloor Temperature | R | 2 | 87 | InputRegister | 300110 | 109 | 10 |  | analog_value | 40111 | degrees_celsius
RegioFlow |  | Flow value | R | 2 | 90 | InputRegister | 300112 | 111 | 10 |  | analog_value | 40027 | no_units
RegioOpenWindowInd |  | Open window indication | L | 2 | 229 | DiscreteInput | 100002 | 1 |  |  | binary_value | 20001
RegioCondensationAlarm |  | Alarm Condensation indication | L | 2 | 230 | DiscreteInput | 100003 | 2 |  |  | binary_value | 20002
RegioPresenceInd |  | Pressens indication | L | 2 | 231 | DiscreteInput | 100004 | 3 |  |  | binary_value | 20003
RegioChangeOverInd |  | Change over indication | L | 2 | 232 | DiscreteInput | 100005 | 4 |  |  | binary_value | 20004
RegioAnaOut1 |  | Analog output 1 | R | 2 | 270 | InputRegister | 300014 | 13 | 1 |  | analog_value | 40015 | volts
RegioAnaOut2 |  | Analog output 2 | R | 2 | 273 | InputRegister | 300015 | 14 | 1 |  | analog_value | 40016 | volts
RegioAnaOut3 |  | Analog output 1 | R | 2 | 276 | InputRegister | 300016 | 15 | 1 |  | analog_value | 40017 | volts
RegioAnaOut4 |  | Analog output 2 | R | 2 | 279 | InputRegister | 300017 | 16 | 1 |  | analog_value | 40018 | volts
RegioHeatSeq1 |  | Control valve Heating 1 | R | 2 | 297 | InputRegister | 300018 | 17 | 1 |  | analog_value | 40019 | percent
RegioHeatSeq2 |  | Control valve Heating 2 | R | 2 | 300 | InputRegister | 300019 | 18 | 1 |  | analog_value | 40020 | percent
RegioCoolSeq1 |  | Control valve Cooling 1 | R | 2 | 303 | InputRegister | 300020 | 19 | 1 |  | analog_value | 40021 | percent
RegioCoolSeq2 |  | Not used | R | 2 | 306 | InputRegister | 300021 | 20 | 1 |  | analog_value | 40022 | percent
RegioHeatCoolOutput |  | Control valve Heating/Cooling | R | 2 | 309 | InputRegister | 300022 | 21 | 1 |  | analog_value | 40023 | percent
RegioVAVOutput |  | Control VAV damper | R | 2 | 312 | InputRegister | 300023 | 22 | 1 |  | analog_value | 40024 | percent
RegioECFanOutput |  | Control EC Fan | R | 2 | 315 | InputRegister | 300024 | 23 | 1 |  | analog_value | 40025 | percent
RegioDigOut1 |  | Digital output 1 | L | 2 | 430 | DiscreteInput | 100006 | 5 |  |  | binary_value | 20005
RegioDigOut2 |  | Digital output 2 | L | 2 | 431 | DiscreteInput | 100007 | 6 |  |  | binary_value | 20006
RegioDigOut3 |  | Digital output 3 | L | 2 | 432 | DiscreteInput | 100008 | 7 |  |  | binary_value | 20007
RegioDigOut4 |  | Digital output 4 | L | 2 | 433 | DiscreteInput | 100009 | 8 |  |  | binary_value | 20008
RegioDigOut5 |  | Digital output 5 | L | 2 | 434 | DiscreteInput | 100010 | 9 |  |  | binary_value | 20009
RegioDigOut6 |  | Digital output 6 | L | 2 | 435 | DiscreteInput | 100011 | 10 |  |  | binary_value | 20010
RegioFanSpeed1Output |  | Start Fan Speed 1 | L | 2 | 443 | DiscreteInput | 100012 | 11 |  |  | binary_value | 20011
RegioFanSpeed2Output |  | Start Fan Speed 2 | L | 2 | 444 | DiscreteInput | 100013 | 12 |  |  | binary_value | 20012
RegioFanSpeed3Output |  | Start Fan Speed 3 | L | 2 | 445 | DiscreteInput | 100014 | 13 |  |  | binary_value | 20013
RegioLightingOutput |  | Start signal Lighting | L | 2 | 446 | DiscreteInput | 100015 | 14 |  |  | binary_value | 20014
RegioSunBlindsInOutput |  | In signal Blind | L | 2 | 447 | DiscreteInput | 100016 | 15 |  |  | binary_value | 20015
RegioSunBlindsOutOutput |  | Out signal Blind | L | 2 | 448 | DiscreteInput | 100017 | 16 |  |  | binary_value | 20016
RegioForcedVentOutput |  | Start forced ventilation | L | 2 | 449 | DiscreteInput | 100018 | 17 |  |  | binary_value | 20017
RegioHeat1IncOutput |  | Increase heat 1 valve | L | 2 | 450 | DiscreteInput | 100019 | 18 |  |  | binary_value | 20018
RegioHeat1DecOutput |  | Decrease heat 1 valve | L | 2 | 451 | DiscreteInput | 100020 | 19 |  |  | binary_value | 20019
RegioHeat1PulsPropOutput |  | Thermal heat 1 valve | L | 2 | 452 | DiscreteInput | 100021 | 20 |  |  | binary_value | 20020
RegioHeat2IncOutput |  | Increase heat 2 valve | L | 2 | 453 | DiscreteInput | 100022 | 21 |  |  | binary_value | 20021
RegioHeat2DecOutput |  | Decrease heat 2 valve | L | 2 | 454 | DiscreteInput | 100023 | 22 |  |  | binary_value | 20022
RegioHeat2PulsPropOutput |  | Thermal heat 2 valve | L | 2 | 455 | DiscreteInput | 100024 | 23 |  |  | binary_value | 20023
RegioCool1IncOutput |  | Increase cool 1 valve | L | 2 | 456 | DiscreteInput | 100025 | 24 |  |  | binary_value | 20024
RegioCool1DecOutput |  | Decrease cool 1 valve | L | 2 | 457 | DiscreteInput | 100026 | 25 |  |  | binary_value | 20025
RegioCool1PulsPropOutput |  | Thermal cool 1 valve | L | 2 | 458 | DiscreteInput | 100027 | 26 |  |  | binary_value | 20026
RegioCool2IncOutput |  | Not used | L | 2 | 459 | DiscreteInput | 100028 | 27 |  |  | binary_value | 20027
RegioCool2DecOutput |  | Not used | L | 2 | 460 | DiscreteInput | 100029 | 28 |  |  | binary_value | 20028
RegioCool2PulsPropOutput |  | Not used | L | 2 | 461 | DiscreteInput | 100030 | 29 |  |  | binary_value | 20029
RegioHeatCoolIncOutput |  | Increase Heat cool valve | L | 2 | 462 | DiscreteInput | 100031 | 30 |  |  | binary_value | 20030
RegioHeatCoolDecOutput |  | Decrease Heat cool valve | L | 2 | 463 | DiscreteInput | 100032 | 31 |  |  | binary_value | 20031
RegioHeatCoolPulsPropOutput |  | Thermal Heat cool valve | L | 2 | 464 | DiscreteInput | 100033 | 32 |  |  | binary_value | 20032
RegioSumAlarm |  | Sum alarm | L | 2 | 465 | DiscreteInput | 100034 | 33 |  |  | binary_value | 20033
RegioSumAlarmA |  | Sum alarm A | L | 2 | 466 | DiscreteInput | 100035 | 34 |  |  | binary_value | 20034
RegioSumAlarmB |  | Sum alarm B | L | 2 | 467 | DiscreteInput | 100036 | 35 |  |  | binary_value | 20035
RegioRoomTemp |  | Room temperature internal or external | R | 2 | 547 | InputRegister | 300025 | 24 | 10 |  | analog_value | 40026 | no_units
RegioRoomTempAverage |  | Average Room temperature internal or external | R | 2 | 553 | InputRegister | 300066 | 65 | 10 |  | analog_value | 40067 | degrees_celsius
RegioAIChangeOverAverage |  | Average Change over Temperature | R | 2 | 556 | InputRegister | 300067 | 66 | 10 |  | analog_value | 40068 | degrees_celsius
RegioOutDoorTempAverage |  | Average Temperature from all controllers | R | 2 | 559 | InputRegister | 300068 | 67 | 10 |  | analog_value | 40069 | degrees_celsius
RegioCondenseAverage |  | Condense Average | R | 2 | 562 | InputRegister | 300069 | 68 | 1 |  | analog_value | 40070 | no_units
RegioRoomCO2Average |  | Average CO2 from all controllers | R | 2 | 565 | InputRegister | 300070 | 69 | 1 |  | analog_value | 40071 | parts_per_million
RegioRoomRHAverage |  | Average Humidity from all controllers | R | 2 | 568 | InputRegister | 300071 | 70 | 1 |  | analog_value | 40072 | percent_relative_humidity
RegioSupplyAirTempAverage |  | Supply Air Temperature from all controllers | R | 2 | 571 | InputRegister | 300072 | 71 | 10 |  | analog_value | 40073 | degrees_celsius
RegioDIOpenWindowCombined |  | Open window indication all Controllers | L | 2 | 574 | DiscreteInput | 100096 | 95 |  |  | binary_value | 20095
RegioDICondenseAlarmCombined |  | Alarm Condense indication all Controllers | L | 2 | 575 | DiscreteInput | 100097 | 96 |  |  | binary_value | 20096
RegioDIPresenceCombined |  | Presence indication all Controllers (This is the combination of all pins not actually the presence state) | L | 2 | 576 | DiscreteInput | 100098 | 97 |  |  | binary_value | 20097
RegioDIChangeoverCombined |  | Change over indication all Controllers | L | 2 | 577 | DiscreteInput | 100099 | 98 |  |  | binary_value | 20098
RegioSetpointOffsetCombined |  | Setpoint Offset , last changed offset from all controllers | R | 2 | 578 | InputRegister | 300073 | 72 | 10 |  | analog_value | 40074 | degrees_celsius
RegioPIDSetP |  | Setpoint Sent to PID | R | 2 | 584 | InputRegister | 300028 | 27 | 10 |  | analog_value | 40029 | degrees_celsius
RegioSetPAdjustment |  | Setpoint Adjustment | R | 2 | 594 | InputRegister | 300029 | 28 | 10 |  | analog_value | 40030 | degrees_celsius
RegioControlState | 3 | Current unit state: 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 4=Bypass | X | 2 | 613 | InputRegister | 300026 | 25 | 1 |  | multi_state_value | 40027
RegioRoomTempControlState |  | Current controller state: 0=Heating 1=Cooling | L | 2 | 614 | DiscreteInput | 100037 | 36 |  |  | binary_value | 20036
RegioHeatCoolSymbol |  | Current controller state: 0=Off 1=Heating 2=Cooling 3=Heating and Cooling | X | 2 | 615 | InputRegister | 300027 | 26 | 1 |  | multi_state_value | 40028
RegioHeatOutput |  | Control signal Heating 0-100 % | R | 2 | 616 | InputRegister | 300030 | 29 | 1 |  | analog_value | 40031 | percent
RegioCoolOutput |  | Control signal Cooling 0-100 % | R | 2 | 619 | InputRegister | 300031 | 30 | 1 |  | analog_value | 40032 | percent
RegioVAVOutputSignal |  | Control signal VAV 0-100% | R | 2 | 622 | InputRegister | 300032 | 31 | 1 |  | analog_value | 40033 | percent
RegioECFanOutputSignal |  | Control signal EC fan 0-100% | R | 2 | 625 | InputRegister | 300033 | 32 | 1 |  | analog_value | 40034 | percent
RegioFanSpeed |  | Current 3speed fan speed: 0=Off 1=Speed1 2=Speed2 3=Speed3 | X | 2 | 628 | InputRegister | 300034 | 33 | 1 |  | multi_state_value | 40035
RegioECFanSpeedIndex |  | Current EC fan speed converted to index, used in RU: 0=Off 1=Speed1 2=Speed2 3=Speed3 | X | 2 | 629 | InputRegister | 300035 | 34 | 1 |  | analog_value | 40036 | no_units
RegioFanSpeedSelectCombined | 4 | Fan speed Selected: 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Forced ventilation 5=Auto | X | 2 | 630 | InputRegister | 300036 | 35 | 1 |  | multi_state_value | 40037
RegioSunBlindsState |  | Blind Position: 0=In 1=Out | L | 2 | 631 | DiscreteInput | 100038 | 37 |  |  | binary_value | 20037
RegioPresence |  | Presence indication | L | 2 | 632 | DiscreteInput | 100039 | 38 |  |  | binary_value | 20038
RegioCO2Presence |  | Is set if presence if CO2 is high | L | 2 | 633 | DiscreteInput | 100040 | 39 |  |  | binary_value | 20039
RegioByPassRunMin |  | Time left in Bypass mode (min) | I | 2 | 634 | InputRegister | 300037 | 36 | 1 |  | analog_value | 40038 | minutes
RegioAIChangeOverState |  | Is set if change over from analog input | L | 2 | 636 | DiscreteInput | 100041 | 40 |  |  | binary_value | 20040
RegioChangeOverState |  | Is set if change over | L | 2 | 637 | DiscreteInput | 100042 | 41 |  |  | binary_value | 20041
RegioRoomTempSensorAlarm |  | Is set if sensor alarm on room sensor (Internal or external) | L | 2 | 638 | DiscreteInput | 100043 | 42 |  |  | binary_value | 20042
RegioTimeGroupOcc |  | Time Group 'Occupied' (No. 1). | L | 2 | 639 | DiscreteInput | 100044 | 43 |  |  | binary_value | 20043
RegioTimeGroupUnOcc |  | Time Group 'Unoccupied' (No. 2). | L | 2 | 640 | DiscreteInput | 100045 | 44 |  |  | binary_value | 20044
RegioTimeGroupLighting |  | Time Group 'Lighting' (No. 3). | L | 2 | 641 | DiscreteInput | 100046 | 45 |  |  | binary_value | 20045
RegioMasterSlaveState |  | Current State in Removable Walls Feature: 0=StandAlone 1=Master 2=Slave 3=Slave with comm error running as standalone | X | 2 | 642 | InputRegister | 300038 | 37 | 1 |  | multi_state_value | 40039
RegioExerciseOnHeat1 |  | Valve Heat 1 in exercise | L | 2 | 672 | DiscreteInput | 100086 | 85 |  |  | binary_value | 20085
RegioExerciseOnHeat2 |  | Valve Heat 2 in exercise | L | 2 | 673 | DiscreteInput | 100087 | 86 |  |  | binary_value | 20086
RegioExerciseOnCool1 |  | Valve Cool 1 in exercise | L | 2 | 674 | DiscreteInput | 100088 | 87 |  |  | binary_value | 20087
RegioExerciseOnCool2 |  | Not used | L | 2 | 675 | DiscreteInput | 100089 | 88 |  |  | binary_value | 20088
RegioExerciseOnHeatCool |  | Valve HeatCool in exercise | L | 2 | 676 | DiscreteInput | 100090 | 89 |  |  | binary_value | 20089
RegioCommFailsafe |  | Communication Failsafe variable, needs to be set to 1 by the Master to indicate communication | L | 2 | 774 | Coil | 94 | 93 |  |  | binary_value | 10009 |  | X
RegioCommFailsafeActive |  | Indicates communication failsafe state | L | 2 | 775 | DiscreteInput | 100100 | 99 |  |  | binary_value | 20099
RegioAnaIn1Aux |  | Analog Input 1 value, when configured as Ext. Analog Input | R | 2 | 780 | InputRegister | 300106 | 105 | 10 |  | analog_value | 40107 | no_units
RegioAnaIn2Aux |  | Analog Input 2 value, when configured as Ext. Analog Input | R | 2 | 783 | InputRegister | 300107 | 106 | 10 |  | analog_value | 40108 | no_units
RegioAnaIn3Aux |  | Analog Input 3 value, when configured as Ext. Analog Input | R | 2 | 786 | InputRegister | 300108 | 107 | 10 |  | analog_value | 40109 | no_units
RegioDigIn1Aux |  | Digital Input 1 value when configured as Ext. Digital Input | L | 2 | 799 | DiscreteInput | 100101 | 100 |  |  | binary_value | 20100
RegioDigIn2Aux |  | Digital Input 2 value when configured as Ext. Digital Input | L | 2 | 800 | DiscreteInput | 100102 | 101 |  |  | binary_value | 20101
RegioDigIn3Aux |  | Digital Input 3 value when configured as Ext. Digital Input | L | 2 | 801 | DiscreteInput | 100103 | 102 |  |  | binary_value | 20102
RegioInput1RU1 |  |  | I | 2 | 898 | InputRegister | 300115 | 114
RegioInput2RU1 |  |  | I | 2 | 900 | InputRegister | 300116 | 115
RegioInput3RU1 |  |  | I | 2 | 902 | InputRegister | 300117 | 116
RegioAi1 |  | Configuration for Analog Input 1 0=Disable 1=External room temp 2=ChangeOver temp 3=Outdoor temp 4=Condensation 5=CO2 sensor 6=RH sensor 11=Supply air Temp 12=Extra zone temperature, room 22 13 External room temp 0-10 V 3 14=Flow sensor 3 101=External room temp room 2 103=Outdoor temp room 2 104=Condensation room 2 105=CO2 sensor room 2 106=RH sensor room 2 111=Supply air temp room 2 112=Extra zone temperature, room 2 2 113=External room temp 0-10 V room 2 3 114=Flow sensor room 2 3 200=Ext. Analog Input PT1000 2 201=Ext. Analog Input 0…10 V 2 | X | 3 | 1 | HoldingRegister | 400144 | 143 | 1
RegioAi2 |  | Configuration for Analog Input 2 | X | 3 | 2 | HoldingRegister | 400145 | 144 | 1
RegioAi3 |  | Configuration for Analog Input 3 | X | 3 | 3 | HoldingRegister | 400146 | 145 | 1
RegioDi1 | 3 | Configuration for Digital Input 1 0=Disable 1=Open window 2=Not Used 3=Presence detector 4=Changeover 101=Open window room 2 102=Not used 103=Presence detector room 2 | X | 3 | 10 | HoldingRegister | 400148 | 147 | 1
RegioDi2 | 1 | Configuration for Digital Input 2 | X | 3 | 11 | HoldingRegister | 400149 | 148 | 1
RegioDi3 |  | Configuration for Digital Input 3 | X | 3 | 12 | HoldingRegister | 400150 | 149 | 1
RegioCI | 1 | Configuration for Digital Condensation Input 1: 0=Disable 1=Regin's KG-A/1 sensor 2=Regin's KG-A/1 sensor room 2 | X | 3 | 22 | HoldingRegister | 400154 | 153 | 1
RegioAo1 | 1 | Configuration for Analog Output 1 0=Disable 1=Heat 2=Heat 2 3=Cool 4=Not used 5=Changeover / 6-Way Valve 6=VAV 7=EC fan 101=Heat room 2 102=Heat 2 room 2 103=Cool room 2 104=Not used 105=Changeover / 6-Way valve room 2 106=VAV room 2 107=EC fan room 2 | X | 3 | 25 | HoldingRegister | 400156 | 155 | 1
RegioAo2 | 3 | Configuration for Analog Output 2 | X | 3 | 26 | HoldingRegister | 400157 | 156 | 1
RegioAo3 | 6 | Configuration for Analog Output 3 | X | 3 | 27 | HoldingRegister | 400158 | 157 | 1
RegioAo4 |  | Configuration for Analog Output 4 | X | 3 | 28 | HoldingRegister | 400159 | 158 | 1
RegioDo1 | 7 | Configuration for Digital Output 1 0 =Disabled 1 =Fan speed 1 2 =Fan speed 2 3 =Fan speed 3 4 =Lighting 5 =Blind in 6 =Blind out 7 =Forced ventilation 8 =Heat valve Inc. 9 =Heat valve Dec 10=Heat valve thermal (PWM) 11=Heat valve 2 Inc. 12=Heat valve 2 Dec. 13=Heat valve 2 thermal (PWM) 14=Cool valve Inc. 15=Cool valve Dec. 16=Cool valve thermal (PWM) 20=Change over valve Inc 21=Change over valve Dec 22=Change over thermal (PWM) 23=SumAlarm 24=SumAlarm A 25=SumAlarm B 26=Heating valve extra zone, thermal (PWM) 2 27= Extra zone active signal 2 101=Fan speed 1 room 2 102=Fan speed 2 room 2 103=Fan speed 3 room 2 104=Lighting room 2 105=Blind in room 2 106=Blind out Room 2 107=Forced ventilation room 2 108=Heat Valve Inc.room 2 109=Heat Valve Dec room 2 110=Heat Valve thermal (PWM) room 2 111=Heat Valve 2 Inc. room 2 112=Heat Valve 2 Dec. room 2 113=Heat Valve 2 Thermal (PWM) room 2 114=Cool Valve Inc. room 2 115=Cool Valve Dec. room 2 116=Cool Valve thermal (PWM) room 2 120=Change over Valve Inc. room 2 121=Change over Valve Dec. room 2 122=Change over Thermal (PWM) room 2 123=SumAlarm room 2 124=SumAlarm A room 2 125=SumAlarm B room 2 126=Heating valve extra zone, thermal (PWM), room 2 2 127= Extra zone active signal, room 2 2 | X | 3 | 34 | HoldingRegister | 400160 | 159 | 1
RegioDo2 | 23 | Configuration for Digital Output 2 | X | 3 | 35 | HoldingRegister | 400161 | 160 | 1
RegioDo3 |  | Configuration for Digital Output 3 | X | 3 | 36 | HoldingRegister | 400162 | 161 | 1
RegioDo4 |  | Configuration for Digital Output 4 | X | 3 | 37 | HoldingRegister | 400163 | 162 | 1
RegioDo5 |  | Configuration for Digital Output 5 | X | 3 | 38 | HoldingRegister | 400164 | 163 | 1
RegioHeatValve1Type |  | Output Signal for HeatValve1: 0=0-10V 1=2-10V 2=10-2V 3=10-0V 4=Inc/Dec 5=PWM(Thermal) 6=6-way valve | X | 3 | 47 | HoldingRegister | 400166 | 165 | 1
RegioHeatValve2Type |  | Output Signal for HeatValve2: | X | 3 | 48 | HoldingRegister | 400167 | 166 | 1
RegioCoolValve1Type |  | Output Signal for CoolValve1: | X | 3 | 49 | HoldingRegister | 400168 | 167 | 1
RegioCoolValve2Type |  | Output Signal for CoolValve2: | X | 3 | 50 | HoldingRegister | 400169 | 168 | 1
RegioHeatCoolValveType |  | Output Signal for ChangeOver/6-WayValve | X | 3 | 51 | HoldingRegister | 400170 | 169 | 1
RegioVAVType |  | Output Signal for VAV | X | 3 | 52 | HoldingRegister | 400171 | 170 | 1
RegioECFANType |  | Output Signal for EC fan | X | 3 | 53 | HoldingRegister | 400172 | 171 | 1
RegioUnderfloorHeatingValveType |  | Underfloor heating valve type 0=0-10 V 1=2-10V 2=10-2 V 3=10-0 V 4=NU 5=PWM (Thermal) | X | 3 | 54 | HoldingRegister | 400479 | 478 | 1 |  | multi_state_value | 30205 |  | X
RegioValveHeat1RunTime | 120 | Run time (sec) closed to opened valve Heat 1 | I | 3 | 67 | HoldingRegister | 400180 | 179 | 1
RegioValveHeat2RunTime | 120 | Run time (sec) closed to opened valve Heat 2 | I | 3 | 69 | HoldingRegister | 400181 | 180 | 1
RegioValveCool1RunTime | 120 | Run time (sec) closed to opened valve Cool 1 | I | 3 | 71 | HoldingRegister | 400182 | 181 | 1
RegioValveCool2RunTime | 120 | Not used | I | 3 | 73 | HoldingRegister | 400183 | 182 | 1
RegioValveHeatCoolRunTime | 120 | Run time (sec) closed to opened valve HeatCool | I | 3 | 75 | HoldingRegister | 400184 | 183 | 1
RegioValveVAVRunTime | 120 | Run time (sec) closed to opened valve VAV | I | 3 | 77 | HoldingRegister | 400185 | 184 | 1
RegioValveECFanRunTime | 120 | Run time (sec) closed to opened valve ECFan | I | 3 | 79 | HoldingRegister | 400186 | 185 | 1
RegioCVDeadbandHeat1 | 2 | Deadband increase/decrease (%) | R | 3 | 101 | HoldingRegister | 400194 | 193 | 1
RegioCVDeadbandHeat2 | 2 | Deadband increase/decrease (%) | R | 3 | 104 | HoldingRegister | 400195 | 194 | 1
RegioCVDeadbandCool1 | 2 | Deadband increase/decrease (%) | R | 3 | 107 | HoldingRegister | 400196 | 195 | 1
RegioCVDeadbandCool2 | 2 | Not used | R | 3 | 110 | HoldingRegister | 400197 | 196 | 1
RegioCVDeadbandHeatCool | 2 | Deadband increase/decrease (%) | R | 3 | 113 | HoldingRegister | 400198 | 197 | 1
RegioCVDeadbandVAV | 2 | Deadband increase/decrease (%) | R | 3 | 116 | HoldingRegister | 400199 | 198 | 1
RegioCVDeadbandECFan | 2 | Deadband increase/decrease (%) | R | 3 | 120 | HoldingRegister | 400200 | 199 | 1
Regio3PointValveStopSignal |  | If enabled it will stop the output digital signal when full open/close. The signal will stop after 1 minute of full open/ close time. This option is applied to all 3 point valves in this system. | L | 3 | 153 | Coil | 26 | 25
RegioPropValveHeat1PeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 163 | HoldingRegister | 400208 | 207 | 1
RegioPropValveHeat2PeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 165 | HoldingRegister | 400209 | 208 | 1
RegioPropValveCool1PeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 167 | HoldingRegister | 400210 | 209 | 1
RegioPropValveCool2PeriodTime | 210 | Not used | I | 3 | 169 | HoldingRegister | 400211 | 210 | 1
RegioPropValveHeatCoolPeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 171 | HoldingRegister | 400212 | 211 | 1
RegioPropValveVAVPeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 173 | HoldingRegister | 400213 | 212 | 1
RegioPropValveECFanPeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 175 | HoldingRegister | 400214 | 213 | 1
RegioPropValveUnderfloorHeatingPeriodTime | 210 | Period time (sec) if thermal control valves | I | 3 | 192 | HoldingRegister | 400480 | 479 | 1 |  | analog_value | 30206 | seconds | X
RegioPropValveHeat1NCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 198 | Coil | 27 | 26
RegioPropValveHeat2NCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 199 | Coil | 28 | 27
RegioPropValveCool1NCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 200 | Coil | 29 | 28
RegioPropValveCool2NCNO |  | Not used | L | 3 | 201 | Coil | 30 | 29
RegioPropValveHeatCoolNCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 202 | Coil | 31 | 30
RegioPropValveVAVNCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 203 | Coil | 32 | 31
RegioPropValveECFanCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 204 | Coil | 33 | 32
RegioPropValveUnderfloorHeatingNCNO |  | Output Type (NC/NO) if thermal control valves | L | 3 | 212 | Coil | 98 | 97 |  |  | binary_value | 10013 |  | X
RegioCVHeatExerciseDay | 8 | Day for exercise heating and heat/cool valve: 0=Never 1-7=mon-sun 8=every day | X | 3 | 215 | HoldingRegister | 400222 | 221 | 1 |  | analog_value | 30062 | no_units | X
RegioCVCoolExerciseDay | 8 | Day for exercise cooling valve: 0=Never 1-7=mon-sun 8=every day | X | 3 | 216 | HoldingRegister | 400223 | 222 | 1 |  | analog_value | 30063 | no_units | X
RegioCVHeatExerciseHour | 15 | Hour for exercise heating and heat/cool valve | X | 3 | 217 | HoldingRegister | 400224 | 223 | 1 |  | analog_value | 30064 | hours | X
RegioCVCoolExerciseHour | 15 | Hour for exercise cooling valve | X | 3 | 218 | HoldingRegister | 400225 | 224 | 1 |  | analog_value | 30065 | hours | X
RegioCVHeatExerciseMin |  | Minute for exercise heating valve | X | 3 | 219 | HoldingRegister | 400226 | 225 | 1
RegioCVCoolExerciseMin |  | Minute for exercise cooling valve | X | 3 | 220 | HoldingRegister | 400227 | 226 | 1
RegioHeatExerciseTime | 120 | Time in seconds to Exercise the Heat Valves | I | 3 | 227 | HoldingRegister | 400228 | 227 | 1 |  | analog_value | 30066 | seconds | X
RegioCoolExerciseTime | 120 | Time in seconds to Exercise the Cool Valves | I | 3 | 229 | HoldingRegister | 400229 | 228 | 1 |  | analog_value | 30067 | seconds | X
RegioSixWayValveFirstSeqFullyOpen |  | 6-way valve tension (V) for fully open on 1st sequence | R | 3 | 235 | HoldingRegister | 400230 | 229 | 10
RegioSixWayValveFirstSeqStartOpen | 3.3 | 6-way valve tension (V) for start open on 1st sequence | R | 3 | 240 | HoldingRegister | 400231 | 230 | 10
RegioSixWayValveSecondSeqStartOpen | 6.7 | 6-way valve tension (V) for start open on 2nd sequence | R | 3 | 243 | HoldingRegister | 400232 | 231 | 10
RegioSixWayValveSecondSeqFullyOpen | 10 | 6-way valve tension (V) for fully open on 2nd sequence | R | 3 | 246 | HoldingRegister | 400233 | 232 | 10
RegioSixWayValveCenterPoint | 5 | 6-way valve tension (V) for center point | R | 3 | 249 | HoldingRegister | 400234 | 233 | 10
RegioSixWayValveCenterPointHyst | 2 | 6-way valve center point hysteresis (%) | X | 3 | 252 | HoldingRegister | 400235 | 234 | 1
RegioSixWayValveSequenceOrder |  | 6-Way Valve Sequence Order: 0=Heat 1st Sequence 1=Heat 2nd Sequence | L | 3 | 253 | Coil | 41 | 40
RegioDi1NC |  | Digital input 1 function : 0=Normally open 1=normally closed | L | 3 | 290 | Coil | 43 | 42
RegioDi2NC |  | Digital input 2 function | L | 3 | 291 | Coil | 44 | 43
RegioDi3NC |  | Digital input 3 function | L | 3 | 292 | Coil | 45 | 44
RegioAi1Comp |  | Analog input 1 compensation | R | 3 | 304 | HoldingRegister | 400250 | 249 | 10 |  | analog_value | 30074 | degrees_celsius | X
RegioAi2Comp |  | Analog input 2 compensation | R | 3 | 307 | HoldingRegister | 400251 | 250 | 10 |  | analog_value | 30075 | degrees_celsius | X
RegioAi3Comp |  | Analog input 3 compensation | R | 3 | 310 | HoldingRegister | 400252 | 251 | 10 |  | analog_value | 30076 | degrees_celsius | X
RegioCond_0V |  | Condense at 0 Volt input | R | 3 | 325 | HoldingRegister | 400254 | 253 | 1
RegioCond_10V | 100 | Condense at 10 Volt input | R | 3 | 328 | HoldingRegister | 400255 | 254 | 1
RegioCO2_0V |  | CO2 at 0 Volt input | R | 3 | 331 | HoldingRegister | 400256 | 255 | 1
RegioCO2_10V | 2000 | CO2 at 10 Volt input | R | 3 | 334 | HoldingRegister | 400257 | 256 | 1
RegioRH_0V |  | RH at 0 Volt input | R | 3 | 337 | HoldingRegister | 400258 | 257 | 1
RegioRH_10V | 100 | RH at 10 Volt input | R | 3 | 340 | HoldingRegister | 400259 | 258 | 1
RegioTempFilterFactor | 0.2 | Filter factor for temperature on analog input: 0=no filter 1=Max filter | R | 3 | 343 | HoldingRegister | 400260 | 259 | 100
RegioCondFilterFactor | 0.2 | Filter factor for condense on analog input: 0=no filter 1=Max filter | R | 3 | 346 | HoldingRegister | 400261 | 260 | 100
RegioCO2FilterFactor | 0.2 | Filter factor for CO2 on analog input: 0=no filter 1=Max filter | R | 3 | 349 | HoldingRegister | 400262 | 261 | 100
RegioRHFilterFactor | 0.2 | Filter factor for RH on analog input: 0=no filter 1=Max filter | R | 3 | 352 | HoldingRegister | 400263 | 262 | 100
RegioInternalTempComp |  | Internal temperature sensor compensation | R | 3 | 355 | HoldingRegister | 400264 | 263 | 10 |  | analog_value | 30078 | degrees_celsius | X
RegioHeat1OutputSelect | 2 | Manual/Auto of Heat1 0=Off 1=Manual 2=Auto | X | 3 | 394 | HoldingRegister | 400276 | 275 | 1 |  | multi_state_value | 30080 |  | X
RegioHeat2OutputSelect | 2 | Manual/Auto of Heat2 | X | 3 | 395 | HoldingRegister | 400277 | 276 | 10 |  | multi_state_value | 30081 |  | X
RegioCoolOutputSelect | 2 | Manual/Auto of Cool1 | X | 3 | 396 | HoldingRegister | 400278 | 277 | 1 |  | multi_state_value | 30082 |  | X
RegioHeatCoolOutputSelect | 2 | Manual/Auto of Heat Cool | X | 3 | 397 | HoldingRegister | 400279 | 278 | 1 |  | multi_state_value | 30083 |  | X
RegioVAVOutputSelect | 2 | Manual/Auto of VAV | X | 3 | 398 | HoldingRegister | 400280 | 279 | 1 |  | multi_state_value | 30084 |  | X
RegioECFanOutputSelect | 2 | Manual/Auto of ECFan | X | 3 | 399 | HoldingRegister | 400281 | 280 | 1 |  | multi_state_value | 30085 |  | X
RegioUnderfloorHeatingSelect | 2 | Manual/Auto of Underfloor heating 0=Off 1=Manual 2=Auto | X | 3 | 406 | HoldingRegister | 400477 | 476 | 1 |  | multi_state_value | 30203 |  | X
RegioHeat1OutputManual |  | Manual value Heat 1 | R | 3 | 411 | HoldingRegister | 400288 | 287 | 1 |  | analog_value | 30092 | percent | X
RegioHeat2OutputManual |  | Manual value Heat 2 | R | 3 | 414 | HoldingRegister | 400289 | 288 | 1 |  | analog_value | 30093 | percent | X
RegioCoolOutputManual |  | Manual value Cool | R | 3 | 417 | HoldingRegister | 400290 | 289 | 1 |  | analog_value | 30094 | percent | X
RegioHeatCoolOutputManual |  | Manual value Heat Cool | R | 3 | 420 | HoldingRegister | 400291 | 290 | 1 |  | analog_value | 30095 | percent | X
RegioVAVOutputManual |  | Manual value VAV | R | 3 | 423 | HoldingRegister | 400292 | 291 | 1 |  | analog_value | 30096 | percent | X
RegioECFanOutputManual |  | Manual value ECFan | R | 3 | 426 | HoldingRegister | 400293 | 292 | 1 |  | analog_value | 30097 | percent | X
RegioUnderfloorHeatingManualValue |  | Manual Value Underfloor heating | R | 3 | 447 | HoldingRegister | 400478 | 477 | 1 |  | analog_value | 30204 | percent | X
RegioLightSelect | 2 | Manual/Auto of Lighting: 0=Off 1=On 2=Auto | X | 3 | 454 | HoldingRegister | 400300 | 299 | 1 |  | multi_state_value | 30104 |  | X
RegioSunBlindsInSelect | 2 | Manual/Auto of BlindIn | X | 3 | 455 | HoldingRegister | 400301 | 300 | 1 |  | multi_state_value | 30105 |  | X
RegioSunBlindsOutSelect | 2 | Manual/Auto of BlindOut | X | 3 | 456 | HoldingRegister | 400302 | 301 | 1 |  | multi_state_value | 30106 |  | X
RegioForcedVentSelect | 2 | Manual/Auto of ForceVentilation | X | 3 | 457 | HoldingRegister | 400303 | 302 | 1 |  | multi_state_value | 30107 |  | X
RegioDigOutSelectSumAlarm | 2 | Manual/Auto of SumAlarm | X | 3 | 458 | HoldingRegister | 400304 | 303 | 1 |  | multi_state_value | 30108 |  | X
RegioDigOutSelectSumAlarmA | 2 | Manual/Auto of SumAlarmA | X | 3 | 459 | HoldingRegister | 400305 | 304 | 1 |  | multi_state_value | 30109 |  | X
RegioDigOutSelectSumAlarmB | 2 | Manual/Auto of SumAlarmB | X | 3 | 460 | HoldingRegister | 400306 | 305 | 1 |  | multi_state_value | 30110 |  | X
RegioFanSelect | 4 | Fan speed Selected Remote/RegioTool: 0=Off 1=Speed1 2=Speed2 3=Speed3 4=Auto | X | 3 | 472 | HoldingRegister | 400314 | 313 | 1 |  | multi_state_value | 30118 |  | X
RegioControllerMode | 9 | Control Mode 0=Heating 1=Heating + Heating 2=Heating + Cooling 3=Cooling 4=Heating/Cooling (change-over) 5=Heating + Heating/Cooling (change-over) 6=Heating + VAV 7=Cooling + VAV 8=VAV 9=Heating + Cooling + VAV | X | 3 | 489 | HoldingRegister | 400002 | 1 | 1 |  | multi_state_value | 40001
RegioHeatSequenceOrder |  | Y1 and Y2 for Heat/Heat: 0=Y1 before Y2 1=Y2 before Y1 | L | 3 | 492 | Coil | 2 | 1
RegioCoolSequenceOrder |  | Y2 and Y3 for Heat/Cool/VAV: 0=Y2 beforeY3 1=Y3 before Y2 | L | 3 | 493 | Coil | 3 | 2
RegioVAVControlType | 2 | Control the VAV output: 0=By temperature 2=By CO2 level 3=By both, the highest need | X | 3 | 496 | HoldingRegister | 400110 | 109 | 1
RegioHeatSetPointOccupied | 22 | Room Base setpoint heating | R | 3 | 516 | HoldingRegister | 400003 | 2 | 10 |  | analog_value | 30001 | degrees_celsius | X
RegioCoolSetPointOccupied | 24 | Room Base setpoint cooling | R | 3 | 519 | HoldingRegister | 400004 | 3 | 10 |  | analog_value | 30002 | degrees_celsius | X
RegioSetPointDeadBandStandby | 3 | Deadband in Standby mode | R | 3 | 522 | HoldingRegister | 400009 | 8 | 10 |  | analog_value | 30007 | degrees_celsius | X
RegioHeatSetPointUnoccupied | 15 | Setpoint heating in Unoccupied | R | 3 | 525 | HoldingRegister | 400007 | 6 | 10 |  | analog_value | 30005 | degrees_celsius | X
RegioCoolSetPointUnoccupied | 30 | Setpoint Cooling in Unoccupied | R | 3 | 528 | HoldingRegister | 400008 | 7 | 10 |  | analog_value | 30006 | degrees_celsius | X
RegioFrostProtectionSetPoint | 8 | Setpoint frost protection | R | 3 | 531 | HoldingRegister | 400010 | 9 | 10 |  | analog_value | 30008 | degrees_celsius | X
RegioRUSetPointAdjPos | 3 | Max allowed offset over setpoint | R | 3 | 534 | HoldingRegister | 400011 | 10 | 1
RegioRUSetPointAdjNeg | 3 | Max allowed offset below setpoint | R | 3 | 537 | HoldingRegister | 400012 | 11 | 1
RegioSetPOffset |  | not used | R | 3 | 540 | HoldingRegister | 400013 | 12 | 10
RegioSetPOffsetRemote |  | Setpoint Offset Remote1 | R | 3 | 543 | HoldingRegister | 400014 | 13 | 10 |  | analog_value | 30009 | degrees_celsius | X
RegioHeatOutputMinLimit |  | Min Limit for Heat Output | R | 3 | 588 | HoldingRegister | 400022 | 21 | 1
RegioHeatOutputMaxLimit | 100 | Max Limit for Heat Output | R | 3 | 591 | HoldingRegister | 400023 | 22 | 1
RegioHeat2OutputMinLimit |  | Min Limit for Heat Output | R | 3 | 594 | HoldingRegister | 400024 | 23 | 1
RegioHeat2OutputMaxLimit | 100 | Max Limit for Heat Output | R | 3 | 597 | HoldingRegister | 400025 | 24 | 1
RegioCool1OutputMinLimit |  | Min Limit for Cool Output | R | 3 | 600 | HoldingRegister | 400026 | 25 | 1
RegioCool1OutputMaxLimit | 100 | Max Limit for Cool Output | R | 3 | 603 | HoldingRegister | 400027 | 26 | 1
RegioCool2OutputMinLimit |  | Not used | R | 3 | 606 | HoldingRegister | 400028 | 27 | 1
RegioCool2OutputMaxLimit | 100 | Not used | R | 3 | 609 | HoldingRegister | 400029 | 28 | 1
RegioVAVOutputMinLimitOff |  | Min Limit for VAV Output at off State | R | 3 | 612 | HoldingRegister | 400030 | 29 | 1 |  | analog_value | 30012 | percent | X
RegioVAVOutputMinLimitUno | 10 | Min Limit for VAV Output at Unoccupied State | R | 3 | 615 | HoldingRegister | 400031 | 30 | 1 |  | analog_value | 30013 | percent | X
RegioVAVOutputMinLimitStandby | 10 | Min Limit for VAV Output at Standby State | R | 3 | 618 | HoldingRegister | 400032 | 31 | 1 |  | analog_value | 30014 | percent | X
RegioVAVOutputMinLimitOcc | 20 | Min Limit for VAV Output at Occupied or Bypass State | R | 3 | 621 | HoldingRegister | 400033 | 32 | 1 |  | analog_value | 30015 | percent | X
RegioVAVOutputMaxLimit | 100 | Max Limit for VAV Output | R | 3 | 624 | HoldingRegister | 400034 | 33 | 1 |  | analog_value | 30016 | percent | X
RegioMaxAirFlowHeatDemand |  | Max Airflow on Heat Demand , if above 0% the max airflow function is enabled | R | 3 | 681 | HoldingRegister | 400039 | 38 | 1
RegioForcedVentControlMode | 3 | Forced Ventilation Control Mode: 0=Off 1=Force Vent on Heat 2=Force Vent on Cool 3=Force Vent on Both Heat and Cool | X | 3 | 693 | HoldingRegister | 400040 | 39 | 1
RegioForcedVentSequence |  | ForcedVentSequence: 0=Forced Ventilation Just 2nd sequence 1=Force Ventilation both sequences | L | 3 | 694 | Coil | 5 | 4
RegioForcedVentAtMaxOutput |  | Forced Ventilation on Max Heat/Cool/Both 0=Off 1=Forced Ventilation on Max Heat 2=Forced Ventilation on Max Cool 3=Forced Ventilation on Max Heat or Cool | X | 3 | 695 | HoldingRegister | 400041 | 40 | 1
RegioRoomTempPBand | 10 | Temperature PID P Band | R | 3 | 708 | HoldingRegister | 400005 | 4 | 1 |  | analog_value | 30003 | no_units | X
RegioRoomTempITime | 300 | Temperature PID I Time | R | 3 | 711 | HoldingRegister | 400006 | 5 | 1 |  | analog_value | 30004 | seconds | X
RegioSupplyAirTempLimCascadeFactor | 3 | Cascade Factor for the Cascade PID | R | 3 | 729 | HoldingRegister | 400042 | 41 | 1 |  | analog_value | 30020 | no_units | X
RegioSupplyAirTempLimHeatMinLimit | 24 | Min Setpoint for the Cascade PID in Heat Mode | R | 3 | 732 | HoldingRegister | 400043 | 42 | 1 |  | analog_value | 30021 | degrees_celsius | X
RegioSupplyAirTempLimHeatMaxLimit | 35 | Max Setpoint for the Cascade PID in Heat Mode | R | 3 | 735 | HoldingRegister | 400044 | 43 | 1 |  | analog_value | 30022 | degrees_celsius | X
RegioSupplyAirTempLimCoolMinLimit | 12 | Min Setpoint for the Cascade PID in Cool Mode | R | 3 | 738 | HoldingRegister | 400045 | 44 | 1 |  | analog_value | 30023 | degrees_celsius | X
RegioSupplyAirTempLimCoolMaxLimit | 24 | Max Setpoint for the Cascade PID in Cool Mode | R | 3 | 741 | HoldingRegister | 400046 | 45 | 1 |  | analog_value | 30024 | degrees_celsius | X
RegioSupplyAirTempLimFrostProtSetPoint | 8 | Supply Air Temp Frost Protection Temperature | R | 3 | 744 | HoldingRegister | 400047 | 46 | 1 |  | analog_value | 30025 | degrees_celsius | X
RegioCO2PBand | 100 | CO2 PID P Band | R | 3 | 776 | HoldingRegister | 400048 | 47 | 1 |  | analog_value | 30026 | no_units | X
RegioCO2ITime | 100 | CO2 PID I Time | R | 3 | 780 | HoldingRegister | 400049 | 48 | 1 |  | analog_value | 30027 | seconds | X
RegioCO2FirstSequence |  | If enabled in modes 7,8 (cool/cool and heat/cool/vav) the CO2 output will override both outputs if the actual output is lower than the CO2 Output by default it only overrides the second sequence | L | 3 | 783 | Coil | 6 | 5
RegioCO2SetPoint | 600 | Setpoint for CO2 PI Controller in PPM | R | 3 | 784 | HoldingRegister | 400050 | 49 | 1 |  | analog_value | 30028 | parts_per_million | X
RegioCO2PresenceDetection | 1 | Activate presence on CO2 | L | 3 | 806 | Coil | 7 | 6
RegioCO2PresenceLimit | 800 | Activate presence if CO2 is higher | R | 3 | 807 | HoldingRegister | 400051 | 50 | 1
RegioCO2PresenceHyst | 160 | Diff for deactivate presence on CO2 | R | 3 | 810 | HoldingRegister | 400052 | 51 | 1
RegioFanControlMode |  | FanControl Mode 0=No control 1=Controlled by Heating 2=Controlled by cooling 3=Controlled by both heat and cooling | X | 3 | 829 | HoldingRegister | 400053 | 52 | 1
RegioFanSpeed1Start | 20 | If higher controller output start fanspeed 1 | X | 3 | 830 | HoldingRegister | 400054 | 53 | 1
RegioFanSpeed2Start | 60 | If higher controller output start fanspeed 2 | X | 3 | 831 | HoldingRegister | 400055 | 54 | 1
RegioFanSpeed3Start | 100 | If higher controller output start fanspeed 3 | X | 3 | 832 | HoldingRegister | 400056 | 55 | 1
RegioFanSpeedHyst | 5 | Hysteresis % for start/stop fan | X | 3 | 833 | HoldingRegister | 400057 | 56 | 1
RegioRUNoOfFanSpeeds | 3 | Configured number of fan speeds (1-3) | X | 3 | 834 | HoldingRegister | 400058 | 57 | 1
RegioMinFanSpeed |  | Min Speed for the fan (0-Stop 1-Speed 1) | L | 3 | 835 | Coil | 8 | 7
RegioFanSwitchTime | 2 | Time (sec) before switching fan speed when changed from RU | I | 3 | 836 | HoldingRegister | 400059 | 58 | 1
RegioECFanMaxLimit | 100 | Max limit for the EC fan (0-100) | R | 3 | 840 | HoldingRegister | 400060 | 59 | 1
RegioECFanMinLimit | 10 | Min limit for the EC fan (0-100) | R | 3 | 843 | HoldingRegister | 400061 | 60 | 1
RegioECFanStartSpeed | 15 | The fan will start at this speed when demand is over the fan speed demand. | R | 3 | 846 | HoldingRegister | 400062 | 61 | 1
RegioFanTypeSelector |  | Type of Fan used , needed for display purposes in the RU. 0=3Speed Fan 1=EC Fan | L | 3 | 849 | Coil | 9 | 8
RegioFanAfterBlowControl |  | If enabled the Fan will work FanStopTime after Heat applied 0=Off 1=Heat1 2=Heat2 3=Heat1 or Heat2 | X | 3 | 850 | HoldingRegister | 400064 | 63 | 1
RegioFanAfterBlowMinSpeed |  | Minimum Fan Speed when FanafterBlow Active | X | 3 | 851 | HoldingRegister | 400065 | 64 | 1 |  | multi_state_value | 30030 |  | X
RegioFanStopTime | 120 | Time (Sec) for the Fan Stop delay when Fan AfterBlow used | I | 3 | 852 | HoldingRegister | 400063 | 62 | 1 |  | analog_value | 30029 | seconds | X
RegioKickStartTime |  | Time (Sec) to Kick Start the Fan, during this time the fan will work at 100%. If 0 this function is not active | I | 3 | 854 | HoldingRegister | 400066 | 65 | 1
RegioBoostMode | 2 | Boost Function will work when on Heating (0) Cooling (1) Both (2) | X | 3 | 899 | HoldingRegister | 400067 | 66 | 1
RegioConfigFanBoostTime |  | Time (sec) [0 to 600 seconds] that the Boost Function is active. If 0 the boost function is disabled | I | 3 | 900 | HoldingRegister | 400068 | 67 | 1
RegioShortStart | 10 | Time (sec) that the Fan runs in Max Speed | I | 3 | 902 | HoldingRegister | 400069 | 68 | 1
RegioBoostPBand | 5 | P-band of the P-Controller of the Fan (just in Boost Startup Mode) | R | 3 | 904 | HoldingRegister | 400070 | 69 | 1
RegioControllerStateReturn | 3 | Select return unit state: 0=Off 1=Unoccupied 2=Stand-by 3=Occupied | X | 3 | 924 | HoldingRegister | 400015 | 14 | 1
RegioControllerStateShutDown | 1 | Select shutdown state : 0=Off 1=Unoccupied 2=Stand-by 3=Occupied | X | 3 | 925 | HoldingRegister | 400016 | 15 | 1
RegioControllerStatePresence | 4 | Presence operating mode: 3=Occupied 4=Bypass | X | 3 | 926 | HoldingRegister | 400017 | 16 | 1
RegioControllerStateRemote | 5 | Is used for remote control: 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 5=No remote control | X | 3 | 927 | HoldingRegister | 400018 | 17 | 1 |  | multi_state_value | 30010 |  | X
RegioControllerStateBypassTime | 120 | Time for Bypass mode (Min) | I | 3 | 930 | HoldingRegister | 400019 | 18 | 1 |  | analog_value | 30011 | minutes | X
RegioPresenceOffDelay | 10 | Off timer for changing to not presence (min) | I | 3 | 932 | HoldingRegister | 400020 | 19 | 1
RegioPresenceOnDelay |  | On timer for changing to presence (min) | I | 3 | 934 | HoldingRegister | 400021 | 20 | 1
RegioLightControlFunction |  | Select light control function 0=Central controlled 1=Local Time controlled 2=Presence controlled 3=Time or Presence controlled 4=Central controlled or Presence controlled | X | 3 | 957 | HoldingRegister | 400071 | 70 | 1 |  | multi_state_value | 30031 |  | X
RegioLightManual |  | Controls the light when central control | L | 3 | 958 | Coil | 10 | 9 |  |  | binary_value | 10001 |  | X
RegioLightingCmdRemote |  | Remote Light Control | L | 3 | 959 | Coil | 11 | 10 |  |  | binary_value | 10002 |  | X
RegioSunBlindsInCmd |  | Command to take in jalousie | L | 3 | 972 | Coil | 12 | 11
RegioSunBlindsOutCmd |  | Command to take out jalousie | L | 3 | 973 | Coil | 13 | 12
RegioSunBlindsRunTime | 240 | Run time for controlling the jalousie in/out (sec) | I | 3 | 974 | HoldingRegister | 400072 | 71 | 1
RegioSunBlindsControl |  | Remote Control for the Jalousie: 0=Go In 1-Stop 2-Go out | X | 3 | 976 | HoldingRegister | 400073 | 72 | 1 |  | multi_state_value | 30032 |  | X
RegioChangeOverSelect | 2 | Select Change Over: 0=heating 1=cooling 2=Auto | X | 3 | 991 | HoldingRegister | 400035 | 34 | 1 |  | multi_state_value | 30017 |  | X
RegioChangeOverType |  | Type of Changeover used in Room 1: 0=Digital (Thermostat) 1=Analog Temperature in Incoming Pipe | L | 3 | 992 | Coil | 4 | 3
RegioChangeOverAIDiffHeat | 3 | The difference between the temperature in the room and the media temperature for change over to cooling | R | 3 | 993 | HoldingRegister | 400036 | 35 | 1 |  | analog_value | 30018 | degrees_celsius | X
RegioChangeOverAIDiffCool | 4 | The difference between the temperature in the room and the media temperature for change over to heating | R | 3 | 996 | HoldingRegister | 400037 | 36 | 1 |  | analog_value | 30019 | degrees_celsius | X
RegioChangeOverValveTime | 600 | The minimum time the valve is opened during change over calculation | I | 3 | 999 | HoldingRegister | 400038 | 37 | 1
RegioRUType |  | Room Unit attached to the controller: 0=None 1=ED-RU 2=ED-RU-O 3=ED-RU-F 4=ED-RU-FO 5=ED-RU-DO 6=ED-RU-DFO 7=ED-RU-DOS 8=ED-RU-H 9=ED-RU-DOCS 10=ED-RUD/ED-RUD-2 | X | 3 | 1010 | HoldingRegister | 400316 | 315 | 1
RegioRUTempUnit | 1 | Display Unit: 0=None 1=°C 2=°F | X | 3 | 1013 | HoldingRegister | 400318 | 317 | 1 |  | multi_state_value | 30120 |  | X
RegioRUTemperatureComp |  | Temperature Compensation for RU 1 | R | 3 | 1014 | HoldingRegister | 400319 | 318 | 1
RegioRUUserELASelection |  | User ELA Selection for Room Unit: 0=Auto Detect | X | 3 | 1017 | HoldingRegister | 400317 | 316 | 1
RegioRUDisplayViewType |  | Select view mode for the display: 0=Display temperature value 1=Heat setpoint 2=Cool setpoint 3=Average cool/heat setpoint 4=Only setpoint offset 5=CO2 Level | X | 3 | 1018 | HoldingRegister | 400320 | 319 | 1
RegioRUDisplaySetPointType |  | Select view mode for the display when pressing increase decrease button: 0=Setpoint offset 1=Controlling setpoint 2=Heat setpoint 3=Cool setpoint | X | 3 | 1020 | HoldingRegister | 400321 | 320 | 1
RegioRUSetPointAdjTimeOut | 5 | Timeout for setpoint adjustment (sec) | X | 3 | 1021 | HoldingRegister | 400322 | 321 | 1
RegioRUMenuTimeOut | 10 | Timeout for menu (sec) | X | 3 | 1022 | HoldingRegister | 400323 | 322 | 1
RegioRUOnOffButtonLongPressTime | 5 | Time (sec) that On/Off button must be pushed before Shutdown state | X | 3 | 1023 | HoldingRegister | 400324 | 323 | 1
RegioRUNoOfSelectMenus | 8 | Number of menus visible in the RU-DOS | X | 3 | 1024 | HoldingRegister | 400325 | 324 | 1
RegioRUNoOfDecimals | 1 | Number of decimal to be showed | X | 3 | 1025 | HoldingRegister | 400326 | 325 | 1
RegioRUDisplayBacklightTime |  | Time for backlight (sec) | I | 3 | 1026 | HoldingRegister | 400327 | 326 | 1
RegioRUButtonsUsed | 7 | Buttons that can be used in the RU | X | 3 | 1028 | HoldingRegister | 400328 | 327 | 1 |  | analog_value | 30121 | no_units | X
RegioRUConfigMenuDisable |  | Enable entering the configuration menu in the RU unit when pressing the UP and Down Key | L | 3 | 1029 | Coil | 49 | 48 |  |  | binary_value | 10005 |  | X
RegioUseRemoteValues | 1 | If 1 it will show in the RU the network avalues from the master controller(All controllers Average) if 0 will display its own room temperature | L | 3 | 1030 | Coil | 50 | 49
RegioRUDisplayBacklightLow | 20 | Lightning Lo (0-255) | X | 3 | 1035 | HoldingRegister | 400329 | 328 | 1
RegioRUDisplayBacklightHigh | 100 | Lightning Hi (0-255) | X | 3 | 1036 | HoldingRegister | 400330 | 329 | 1
RegioRUDisplayContrast | 15 | Contrast (0-15) | X | 3 | 1037 | HoldingRegister | 400331 | 330 | 1
RegioAlarmHyst | 0.2 | Alarm hysteresis | R | 3 | 1127 | HoldingRegister | 400350 | 349 | 10 |  | analog_value | 30124 | no_units | X
RegioRoomTempHighLimit | 40 | High room temp | R | 3 | 1130 | HoldingRegister | 400351 | 350 | 1 |  | analog_value | 30125 | no_units | X
RegioRoomTempLowLimit | 15 | Low room temp | R | 3 | 1133 | HoldingRegister | 400352 | 351 | 1 |  | analog_value | 30126 | no_units | X
RegioRoomTempMaxDeviationLimit | 20 | Max allowed difference between setpoint and room temp before alarm | R | 3 | 1136 | HoldingRegister | 400353 | 352 | 1 |  | analog_value | 30127 | no_units | X
RegioCO2MaxLimit | 1500 | Max CO2 Level for Alarm | R | 3 | 1152 | HoldingRegister | 400362 | 361 | 1 |  | analog_value | 30136 | parts_per_million | X
RegioCondenseLimit | 80 | High limit for condense alarm | R | 3 | 1167 | HoldingRegister | 400358 | 357 | 1 |  | analog_value | 30132 | no_units | X
RegioCondenseHyst | 2 | Condense alarm hysteresis | R | 3 | 1170 | HoldingRegister | 400359 | 358 | 1 |  | analog_value | 30133 | no_units | X
RegioDisable2ndSequence |  | If enabled when Condensation input is active in modes with 2 sequences the 2nd sequence will also be set to 0% | L | 3 | 1173 | Coil | 57 | 56
RegioPort1Func | 2 | Defines the function for Port1: 0=Not used 1=Exoline Master 2=Exoline Slave 3=Modbus Master 4= Modbus Slave 5=BACnet 6=Room Unit Display | X | 3 | 1192 | HoldingRegister | 400364 | 363 | 1
RegioPort2Func | 1 | Defines the function for Port2: 0=Not used 1=Exoline Master 2=Exoline Slave 3=Modbus Master 4= Modbus Slave 5=BACnet 6=Room Unit Display | X | 3 | 1193 | HoldingRegister | 400369 | 368 | 1
RegioPort1Parity | 1 | Port 1 Parity 0=No Parity 1=Odd 2=Even | X | 3 | 1194 | HoldingRegister | 400366 | 365 | 1
RegioPort2Parity | 1 | Port 1 Parity 0=No Parity 1=Odd 2=Even | X | 3 | 1195 | HoldingRegister | 400371 | 370 | 1
RegioBaud_Port_1 |  | Bit rate Port 1 | X | 3 | 1196 | HoldingRegister | 400365 | 364 | 1
RegioTimeOut_Port_1 |  | Port 1 Timeout | X | 3 | 1197 | HoldingRegister | 400367 | 366 | 1
RegioCharTimeOut_Port_1 |  | Port 1 Char Time Out | I | 3 | 1198 | HoldingRegister | 400368 | 367 | 1
RegioBaud_Port_2 |  | Bit rate Port 2 | X | 3 | 1200 | HoldingRegister | 400370 | 369 | 1
RegioTimeOut_Port_2 |  | Port 2 Timeout | X | 3 | 1201 | HoldingRegister | 400372 | 371 | 1
RegioCharTimeOut_Port_2 |  | Port 2 Char Time Out | I | 3 | 1202 | HoldingRegister | 400373 | 372 | 1
RegioMasterPort |  | - | X | 3 | 1204 | HoldingRegister | 400374 | 373 | 1
RegioRouterDefaultRoute | 2 | - | X | 3 | 1205 | HoldingRegister | 400375 | 374 | 1
RegioMin_PLA |  | - | X | 3 | 1206 | HoldingRegister | 400376 | 375 | 1
RegioMax_PLA | 255 | - | X | 3 | 1207 | HoldingRegister | 400377 | 376 | 1
RegioMin_ELA |  | - | X | 3 | 1208 | HoldingRegister | 400378 | 377 | 1
RegioMax_ELA | 255 | - | X | 3 | 1209 | HoldingRegister | 400379 | 378 | 1
RegioTcpIpMasterAddrCommit | 1 | - | L | 3 | 1249 | Coil | 59 | 58
RegioTCPIPMasterAnswerTimeout | 25 | - | I | 3 | 1250 | HoldingRegister | 400380 | 379 | 1
RegioModbusIpEnable | 1 | Enables Modbus IP | L | 3 | 1269 | Coil | 60 | 59
RegioModbusSlaveAddr | 1 | Modbus slave address | X | 3 | 1270 | HoldingRegister | 400381 | 380 | 1
RegioBACnetIpEnable | 1 | Enables BACnet IP datalink | L | 3 | 1280 | Coil | 61 | 60
RegioRemovableWallsMaster |  | Set to 1 to enable master Multiple Controllers on Port Define on RemovableWallsCommPort | L | 3 | 1300 | Coil | 64 | 63
RegioRemovableWallsSlave |  | Set to 1 to enable slave Multiple Controllers on Port Define on RemovableWallsCommPort | L | 3 | 1301 | Coil | 65 | 64
RegioUseMasterValues |  | Set to 1 to enable Removable walls but only use the master sensors values to feed into the control loop | L | 3 | 1302 | Coil | 66 | 65
RegioRemovableWallsCommPort |  | Port used for multiple controllers | X | 3 | 1303 | HoldingRegister | 400383 | 382 | 1
RegioRemovableWallsNSlaves |  | Number of slaves in the Network Max 4 | X | 3 | 1304 | HoldingRegister | 400384 | 383 | 1
RegioRemovableWallsPLASlaves(0) |  | PLA Address Slaves | X | 3 | 1305 | HoldingRegister | 400385 | 384 | 1
RegioRemovableWallsPLASlave1 | 254 | PLA Slave 1 | X | 3 | 1306 | HoldingRegister | 400386 | 385 | 1
RegioRemovableWallsPLASlave2 | 254 | PLA Slave 2 | X | 3 | 1307 | HoldingRegister | 400387 | 386 | 1
RegioRemovableWallsPLASlave3 | 254 | PLA Slave 3 | X | 3 | 1308 | HoldingRegister | 400388 | 387 | 1
RegioRemovableWallsPLASlave4 | 254 | PLA Slave 4 | X | 3 | 1309 | HoldingRegister | 400389 | 388 | 1
RegioRemovableWallsELASlaves(0) |  | ELA Address Slaves | X | 3 | 1310 | HoldingRegister | 400390 | 389 | 1
RegioRemovableWallsELASlave1 | 31 | ELA Slave 1 | X | 3 | 1311 | HoldingRegister | 400391 | 390 | 1
RegioRemovableWallsELASlave2 | 32 | ELA Slave 2 | X | 3 | 1312 | HoldingRegister | 400392 | 391 | 1
RegioRemovableWallsELASlave3 | 33 | ELA Slave 3 | X | 3 | 1313 | HoldingRegister | 400393 | 392 | 1
RegioRemovableWallsELASlave4 | 34 | ELA Slave 4 | X | 3 | 1314 | HoldingRegister | 400394 | 393 | 1
RegioNRetries | 3 | Number of retries to read/write var from/to slaves | X | 3 | 1315 | HoldingRegister | 400395 | 394 | 1
RegioSlaveCommTimeOut | 3 | Minutes with missed communication from master to a slave consider that there is a comm failure and revert back to control its own outputs | I | 3 | 1316 | HoldingRegister | 400396 | 395 | 1
RegioRemoteDIOpenWindow |  | Communication Open Window State | L | 3 | 1335 | Coil | 87 | 86
RegioRemoteDIPresence |  | Communication Presence State | L | 3 | 1336 | Coil | 88 | 87
RegioRemoteDIChangeover |  | Communication ChangeOver State | L | 3 | 1337 | Coil | 89 | 88
RegioRemoteDICondenseAlarm |  | Communication Condensation State | L | 3 | 1338 | Coil | 90 | 89
RegioRemoteDIOpenWindowSelect |  | Open Window Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1342 | Coil | 80 | 79
RegioRemoteDIPresenceSelect |  | Presence Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1343 | Coil | 81 | 80
RegioRemoteDIChangeoverSelect |  | ChangeOver State Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1344 | Coil | 82 | 81
RegioRemoteDICondenseAlarmSelect |  | Condensation State Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1345 | Coil | 83 | 82
RegioRemoteRoomTemp |  | Communication Room Temperature Value | R | 3 | 1349 | HoldingRegister | 400397 | 396 | 10
RegioRemoteAIChangeOver |  | Communication Changeover Temperature Value | R | 3 | 1352 | HoldingRegister | 400398 | 397 | 10
RegioRemoteOutDoorTemp |  | Communication Outdoor Temperature Value | R | 3 | 1355 | HoldingRegister | 400399 | 398 | 10
RegioRemoteCondense |  | Communication Condensation Value | R | 3 | 1358 | HoldingRegister | 400400 | 399 | 1
RegioRemoteRoomCO2 |  | Communication CO2 Value | R | 3 | 1361 | HoldingRegister | 400401 | 400 | 1
RegioRemoteRoomRH |  | Communication RH Value | R | 3 | 1364 | HoldingRegister | 400402 | 401 | 1
RegioRemoteSupplyAir |  | Communication Supply Air Temperature Value | R | 3 | 1367 | HoldingRegister | 400403 | 402 | 10
RegioRemoteUnderfloortemp |  | Communication Underfloor Temperature Value | R | 3 | 1389 | HoldingRegister | 400476 | 475 | 10 |  | analog_value | 30202 | degrees_celsius | X
RegioRemoteRoomTempSelect |  | Room Temperature Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1395 | Coil | 67 | 66
RegioRemoteAIChangeOverSelect |  | ChangeOver Temperature Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1396 | Coil | 68 | 67
RegioRemoteOutDoorTempSelect |  | Outdoor Temperature Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1397 | Coil | 69 | 68
RegioRemoteCondenseSelect |  | Condensation Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1398 | Coil | 70 | 69
RegioRemoteRoomCO2Select |  | CO2 Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1399 | Coil | 71 | 70
RegioRemoteRoomRHSelect |  | RH Temperature Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1400 | Coil | 72 | 71
RegioRemoteSupplyAirSelect |  | Supply Air Temperature Source Selector: 0=Use Controller Input Values 1=use remote values (Exoline/Modbus/BACnet) | L | 3 | 1401 | Coil | 73 | 72
RegioRemoteUnderfloorTempSelect |  | Underfloor heating temperature source selector 0= Use controller input values 1= Use remote values (Exoline/Modbus/BACnet) | L | 3 | 1408 | Coil | 97 | 96 |  |  | binary_value | 10012 |  | X
RegioLogActive | 1 | Activate log function for EXOScada | L | 3 | 1443 | Coil | 62 | 61
RegioAlarmActive | 3 | Activate alarm and events function for EXOScada 0=Not active 1=Only alarm 2=Only events 3=Alarm and events is active | X | 3 | 1444 | HoldingRegister | 400382 | 381 | 1
RegioAutoSummerTime | 1 | Switch automatically between summer and winter time | L | 3 | 1445 | Coil | 63 | 62 |  |  | binary_value | 10008 |  | X
RegioEnableCommFailsafe |  | Enables/Disables the communication Failsafe function 0= Disable 1= Enable | L | 3 | 1450 | Coil | 95 | 94 |  |  | binary_value | 10010 |  | X
RegioFailsafetime | 10 | Communication failure safe time for triggering Failsafe | X | 3 | 1451 | HoldingRegister | 400455 | 454 | 1 |  | analog_value | 30181 | minutes | X
RegioFailsafeState |  | State the controller will revert to if communication Failsafe is active 0=Off 1=Unoccupied 2=Stand-by 3=Occupied 4=Bypass 5=Keep Current | X | 3 | 1452 | HoldingRegister | 400456 | 455 | 1 |  | multi_state_value | 30182 |  | X
RegioVAVOutputMinLimitBypass | 20 | Min Limit for VAV Output at Bypass State | R | 3 | 1453 | HoldingRegister | 400470 | 469 | 1 |  | analog_value | 30196 | percent | X
RegioAnalog1Select | 2 | Manual Selection for Analog Output 1 0=Off 1=Manual 2=Auto | X | 3 | 1459 | HoldingRegister | 400457 | 456 | 1 |  | multi_state_value | 30183 |  | X
RegioAnalog2Select | 2 | Manual Selection for Analog Output 2 | X | 3 | 1460 | HoldingRegister | 400458 | 457 | 1 |  | multi_state_value | 30184 |  | X
RegioAnalog3Select | 2 | Manual Selection for Analog Output 3 | X | 3 | 1461 | HoldingRegister | 400459 | 458 | 1 |  | multi_state_value | 30185 |  | X
RegioAnalog4Select | 2 | Manual Selection for Analog Output 4 | X | 3 | 1462 | HoldingRegister | 400460 | 459 | 1 |  | multi_state_value | 30186 |  | X
RegioAnalog1ManualValue |  | Analog Manual Value for Analog Output 1 | R | 3 | 1469 | HoldingRegister | 400461 | 460 | 10 |  | analog_value | 30187 | volts | X
RegioAnalog2ManualValue |  | Analog Manual Value for Analog Output 2 | R | 3 | 1472 | HoldingRegister | 400462 | 461 | 10 |  | analog_value | 30188 | volts | X
RegioAnalog3ManualValue |  | Analog Manual Value for Analog Output 3 | R | 3 | 1475 | HoldingRegister | 400463 | 462 | 10 |  | analog_value | 30189 | volts | X
RegioAnalog4ManualValue |  | Analog Manual Value for Analog Output 4 | R | 3 | 1478 | HoldingRegister | 400464 | 463 | 10 |  | analog_value | 30190 | volts | X
RegioDigital1Select | 2 | Manual Selection for Digital Output 1 0=Off 1=On 2=Auto | X | 3 | 1499 | HoldingRegister | 400465 | 464 | 1 |  | multi_state_value | 30191 |  | X
RegioDigital2Select | 2 | Manual Selection for Digital Output 2 | X | 3 | 1500 | HoldingRegister | 400466 | 465 | 1 |  | multi_state_value | 30192 |  | X
RegioDigital3Select | 2 | Manual Selection for Digital Output 3 | X | 3 | 1501 | HoldingRegister | 400467 | 466 | 1 |  | multi_state_value | 30193 |  | X
RegioDigital4Select | 2 | Manual Selection for Digital Output 4 | X | 3 | 1502 | HoldingRegister | 400468 | 467 | 1 |  | multi_state_value | 30194 |  | X
RegioDigital5Select | 2 | Manual Selection for Digital Output 5 | X | 3 | 1503 | HoldingRegister | 400469 | 468 | 1 |  | multi_state_value | 30195 |  | X
RegioUnderfloorHeatingSetpoint | 22 | Room Setpoint for underfloor heating | R | 3 | 1514 | HoldingRegister | 400472 | 471 | 10 |  | analog_value | 30198 | degrees_celsius | X
RegioUnderfloorHeatingEnable |  | Underfloor Enable Condition | X | 3 | 1517 | HoldingRegister | 400473 | 472 | 1 |  | multi_state_value | 30199 |  | X
RegioUnderfloorHeatingPBand | 10 | Underfloor heating PI Control P Band | R | 3 | 1518 | HoldingRegister | 400474 | 473 | 1 |  | analog_value | 30200 | no_units | X
RegioUnderfloorHeatingITime | 300 | Underfloor heating PI Control I Time | R | 3 | 1521 | HoldingRegister | 400475 | 474 | 1 |  | analog_value | 30201 | seconds | X
RegioUnderfloorHeatingDisableCooling | 1 | Disable underfloor heating when main aera is cooling | L | 3 | 1524 | Coil | 96 | 95 |  |  | binary_value | 10011 |  | X
RegioResetRUSettingsOnShutdow |  | Enables reset of user inputs on shutdown 0= Disable 1= Enable | L | 3 | 1536 | Coil | 102 | 101 |  |  | binary_value | 10017 |  | X
RegioECFanAtForcedVentilation |  | EC Fan speed at forced ventilation | R | 3 | 1538 | HoldingRegister | 400490 | 489 | 1 |  | analog_value | 30216 | percent | X
RegioFanButtonBehaviour |  | Fan Button Behavior 0=Manual fan control (default setting) 1=Activates forced ventilation | L | 3 | 1544 | Coil | 104 | 103 |  |  | binary_value | 10019 |  | X
RegioRoomtemp_0V |  | Room temperature at 0 Volt input | R | 3 | 1553 | HoldingRegister | 400492 | 491 | 1
RegioRoomtemp_10V | 100 | Room temperature at 10 Volt input | R | 3 | 1556 | HoldingRegister | 400493 | 492 | 1
RegioFlow_0V |  | Air flow at 0 Volt input | R | 3 | 1560 | HoldingRegister | 400494 | 493 | 1
RegioFlow_10V | 100 | Air flow at 10 Volt input | R | 3 | 1563 | HoldingRegister | 400495 | 494 | 1
RegioRoomtempFilterFactor | 0.2 | Filter factor for room temperature on analog input 0=no filter 1=Max filter | R | 3 | 1566 | HoldingRegister | 400496 | 495 | 100
RegioFlowFilterFactor | 0.2 | Filter factor for air flow on analog input 0=no filter 1=Max filter | R | 3 | 1569 | HoldingRegister | 400497 | 496 | 100
RegioOutput1RU1 |  |  | I | 3 | 1590 | HoldingRegister | 400506 | 505
RegioOutput2RU1 |  |  | I | 3 | 1592 | HoldingRegister | 400507 | 506
RegioOutput3RU1 |  |  | I | 3 | 1594 | HoldingRegister | 400508 | 507
AlaAcknow | 255 | External acknowledge command | X | 37 | 1 | HoldingRegister | 400446 | 445 | 1 |  | analog_value | 30172 | no_units | X
AlaBlock | 255 | External blocking command | X | 37 | 2 | HoldingRegister | 400447 | 446 | 1 |  | analog_value | 30173 | no_units | X
AlaUnBlock | 255 | External unblocking command | X | 37 | 3 | HoldingRegister | 400448 | 447 | 1 |  | analog_value | 30174 | no_units | X
AlaPt1_Status |  | Status for point no. 1 Presence 0=Not used 1=Normal 2=Blocked 3=Acknowledge 4=Not used 5=Cancelled 6=Not used 7=Alarm | X | 39 | 1 | InputRegister | 300074 | 73 | 1 |  | multi_state_value | 40075
AlaPt2_Status |  | Status for point no. 2 OpenWindow | X | 39 | 2 | InputRegister | 300075 | 74 | 1 |  | multi_state_value | 40076
AlaPt3_Status |  | Status for point no. 3 Condensation | X | 39 | 3 | InputRegister | 300076 | 75 | 1 |  | multi_state_value | 40077
AlaPt4_Status |  | Status for point no. 4 RoomTempHigh | X | 39 | 4 | InputRegister | 300077 | 76 | 1 |  | multi_state_value | 40078
AlaPt5_Status |  | Status for point no. 5 RoomTempLow | X | 39 | 5 | InputRegister | 300078 | 77 | 1 |  | multi_state_value | 40079
AlaPt6_Status |  | Status for point no. 6 RoomTempDeviation | X | 39 | 6 | InputRegister | 300079 | 78 | 1 |  | multi_state_value | 40080
AlaPt7_Status |  | Status for point no. 7 RoomControllerInManualMode | X | 39 | 7 | InputRegister | 300080 | 79 | 1 |  | multi_state_value | 40081
AlaPt8_Status |  | Status for point no. 8 SensorAlarm | X | 39 | 8 | InputRegister | 300081 | 80 | 1 |  | multi_state_value | 40082
AlaPt9_Status |  | Status for point no. 9 RoomUnitError | X | 39 | 9 | InputRegister | 300082 | 81 | 1 |  | multi_state_value | 40083
AlaPt19_Status |  | Status for point no. 19 Slave1CommFail | X | 39 | 19 | InputRegister | 300092 | 91 | 1 |  | multi_state_value | 40093
AlaPt20_Status |  | Status for point no. 20 Slave2CommFail | X | 39 | 20 | InputRegister | 300093 | 92 | 1 |  | multi_state_value | 40094
AlaPt21_Status |  | Status for point no. 21 Slave3CommFail | X | 39 | 21 | InputRegister | 300094 | 93 | 1 |  | multi_state_value | 40095
AlaPt22_Status |  | Status for point no. 22 Slave4CommFail | X | 39 | 22 | InputRegister | 300095 | 94 | 1 |  | multi_state_value | 40096
AlaPt23_Status |  | Status for point no. 23 MasterCommFail | X | 39 | 23 | InputRegister | 300096 | 95 | 1 |  | multi_state_value | 40097
AlaPt24_Status |  | Status for point no. 24 SlaveNormalOperation | X | 39 | 24 | InputRegister | 300097 | 96 | 1 |  | multi_state_value | 40098
AlaPt25_Status |  | Status for point no. 25 CO2 Level High | X | 39 | 25 | InputRegister | 300098 | 97 | 1 |  | multi_state_value | 40099
AlaPt27_Status |  | Status for point no. 27 Communication fail safe | X | 39 | 27 | InputRegister | 300100 | 99 | 1 |  | multi_state_value | 40101
AlaPt28_Status |  | Status for point no. 28 Hardware Manual Operation | X | 39 | 28 | InputRegister | 300101 | 100 | 1 |  | multi_state_value | 40102
AlaPt29_Status |  | Status for point no. 29 External Alarm Digital input 1 | X | 39 | 29 | InputRegister | 300102 | 101 | 1 |  | multi_state_value | 40103
AlaPt30_Status |  | Status for point no. 30 External Alarm Digital input 2 | X | 39 | 30 | InputRegister | 300103 | 102 | 1 |  | multi_state_value | 40104
AlaPt31_Status |  | Status for point no. 31 External Alarm Digital input 3 | X | 39 | 31 | InputRegister | 300104 | 103 | 1 |  | multi_state_value | 40105
AlaPt33_Status |  | Status for point no. 33 Battery Failure | X | 39 | 33 | InputRegister | 300114 | 113 | 1 |  | multi_state_value | 40107
AlaPt1_DelayValue |  | Delay value for point no. 1 Presence 0=Not used 1=Normal 2=Blocked 3=Acknowledge 4=Not used 5=Cancelled 6=Not used 7=Alarm | I | 39 | 70 | HoldingRegister | 400420 | 419 | 1 |  | analog_value | 30146 | no_units | X
AlaPt2_DelayValue |  | Delay value for point no. 2 OpenWindow | I | 39 | 72 | HoldingRegister | 400421 | 420 | 1 |  | analog_value | 30147 | no_units | X
AlaPt3_DelayValue |  | Delay value for point no. 3 Condensation | I | 39 | 74 | HoldingRegister | 400422 | 421 | 1 |  | analog_value | 30148 | no_units | X
AlaPt4_DelayValue |  | Delay value for point no. 4 RoomTempHigh | I | 39 | 76 | HoldingRegister | 400423 | 422 | 1 |  | analog_value | 30149 | no_units | X
AlaPt5_DelayValue |  | Delay value for point no. 5 RoomTempLow | I | 39 | 78 | HoldingRegister | 400424 | 423 | 1 |  | analog_value | 30150 | no_units | X
AlaPt6_DelayValue |  | Delay value for point no. 6 RoomTempDeviation | I | 39 | 80 | HoldingRegister | 400425 | 424 | 1 |  | analog_value | 30151 | no_units | X
AlaPt7_DelayValue |  | Delay value for point no. 7 RoomControllerInManualMode | I | 39 | 82 | HoldingRegister | 400426 | 425 | 1 |  | analog_value | 30152 | no_units | X
AlaPt8_DelayValue |  | Delay value for point no. 8 SensorAlarm | I | 39 | 84 | HoldingRegister | 400427 | 426 | 1 |  | analog_value | 30153 | no_units | X
AlaPt9_DelayValue |  | Delay value for point no. 9 RoomUnitError | I | 39 | 86 | HoldingRegister | 400428 | 427 | 1 |  | analog_value | 30154 | no_units | X
AlaPt19_DelayValue |  | Delay value for point no. 19 Slave1CommFail | I | 39 | 106 | HoldingRegister | 400438 | 437 | 1 |  | analog_value | 30164 | no_units | X
AlaPt20_DelayValue |  | Delay value for point no. 20 Slave2CommFail | I | 39 | 108 | HoldingRegister | 400439 | 438 | 1 |  | analog_value | 30165 | no_units | X
AlaPt21_DelayValue |  | Delay value for point no. 21 Slave3CommFail | I | 39 | 110 | HoldingRegister | 400440 | 439 | 1 |  | analog_value | 30166 | no_units | X
AlaPt22_DelayValue |  | Delay value for point no. 22 Slave4CommFail | I | 39 | 112 | HoldingRegister | 400441 | 440 | 1 |  | analog_value | 30167 | no_units | X
AlaPt23_DelayValue |  | Delay value for point no. 23 MasterCommFail | I | 39 | 114 | HoldingRegister | 400442 | 441 | 1 |  | analog_value | 30168 | no_units | X
AlaPt24_DelayValue |  | Delay value for point no. 24 SlaveNormalOperation | I | 39 | 116 | HoldingRegister | 400443 | 442 | 1 |  | analog_value | 30169 | no_units | X
AlaPt25_DelayValue | 10 | Delay value for point no. 25 CO2 Level High | I | 39 | 118 | HoldingRegister | 400444 | 443 | 1 |  | analog_value | 30170 | no_units | X
AlaPt27_DelayValue |  | Delay value for point no. 27 Communication fail safe | I | 39 | 122 | HoldingRegister | 400449 | 448 | 1 |  | analog_value | 30175 | no_units | X
AlaPt28_DelayValue |  | Delay value for point no. 28 Hardware Manual Operation | I | 39 | 124 | HoldingRegister | 400450 | 449 | 1 |  | analog_value | 30176 | no_units | X
AlaPt29_DelayValue |  | Delay value for point no. 29 External Alarm Digital Input 1 | I | 39 | 126 | HoldingRegister | 400451 | 450 | 1 |  | analog_value | 30177 | no_units | X
AlaPt30_DelayValue |  | Delay value for point no. 30 External Alarm Digital Input 2 | I | 39 | 128 | HoldingRegister | 400452 | 451 | 1 |  | analog_value | 30178 | no_units | X
AlaPt31_DelayValue |  | Delay value for point no. 31 External Alarm Digital Input 3 | I | 39 | 130 | HoldingRegister | 400453 | 452 | 1 |  | analog_value | 30179 | no_units | X
AlaPt33_DelayValue |  | Delay value for point no. 33 Battery Failure | I | 39 | 134 | HoldingRegister | 400505 | 504 | 1 |  | analog_value | 30182 | no_units | X
PLA | 254 | Controller PLA Address | X | 241 | 0 | HoldingRegister | 400418 | 417 | 1
ELA | 30 | Controller ELA Address | X | 241 | 1 | HoldingRegister | 400419 | 418 | 1
Sec |  | System Time Seconds | X | 241 | 4 | HoldingRegister | 400410 | 409 | 1 |  | analog_value | 30138 | seconds | X
Minute |  | System Time Minutes | X | 241 | 5 | HoldingRegister | 400411 | 410 | 1 |  | analog_value | 30139 | minutes | X
Hour |  | System Time Hours | X | 241 | 6 | HoldingRegister | 400412 | 411 | 1 |  | analog_value | 30140 | hours | X
WDay |  | System Weekday | X | 241 | 7 | HoldingRegister | 400413 | 412 | 1 |  | analog_value | 30141 | no_units | X
Week |  | System Week | X | 241 | 8 | HoldingRegister | 400414 | 413 | 1 |  | analog_value | 30142 | no_units | X
Date |  | System Date Day | X | 241 | 9 | HoldingRegister | 400415 | 414 | 1 |  | analog_value | 30143 | no_units | X
Month |  | System Date Month | X | 241 | 10 | HoldingRegister | 400416 | 415 | 1 |  | analog_value | 30144 | no_units | X
Year |  | System Date Year | X | 241 | 11 | HoldingRegister | 400417 | 416 | 1 |  | analog_value | 30145 | no_units | X