## Variables
RTX-2.0-1-02 ꟷ Variable list | [15 empty] | Revision: | A
|  |  | EXOline |  |  | Modbus | [6 empty] | BACnet
Name | Default | Description | Type | Load | Cell | Reg. Type | RW | Register | Addr | Data Type | Scale | Offset | Object type | Instance | Unit | Writeable | Variable type
ModbusListVersion |  | Modbus list version | X | 1 | 0 | Input | R | 300001 | 0 | U8
product_reset | 0 | Write to this register will trigger resets with different reset reasons | I | 1 | 1
rc_wink | 0 | Wink for this amount of time in seconds | X | 1 | 3 | Holding | RW | 400003 | 2 | U8 |  |  | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 | Commit communication settings | L | 1 | 5 | Coil | RW | 000001 | 0 | LOGIC |  |  | binary_value | 9001 |  | X
RC_Port1Mode | 2 | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | RW | 400005 | 4 | U8 |  |  | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | RW | 400007 | 6 | U8 |  |  | multi_state_value | 9101 |  | X
RC_Port1Format | 112 | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | RW | 400006 | 5 | U8 |  |  | multi_state_value | 9201 |  | X
SerialHigh |  | Serial number, high part | I | 1 | 15 | Input | R | 300005 | 4 | I16
SerialMid |  | Serial number, mid part | I | 1 | 17 | Input | R | 300004 | 3 | I16
SerialLow |  | Serial number, low part | I | 1 | 19 | Input | R | 300003 | 2 | I16
RC_Offline |  | Heartbeat function indicates if the device is offline or not | L | 1 | 21 | Discrete | R | 100001 | 0 | LOGIC
RC_OfflineTrigger | 0 | Write 1 to this register periodically for keep system running in normal mode, will be set to 0 by application | L | 1 | 22 | Coil | RW | 000002 | 1 | LOGIC |  |  | binary_value | 9101 |  | X
RC_OfflineFunction | 0 | Offline function | X | 1 | 23 | Holding | RW | 400020 | 19 | U8 |  |  | multi_state_value | 9301 |  | X
RC_OfflineCounter |  | Offline timeout counter seconds. Used to check current state of the counter, it counts from 0 at trigger up to next trigger or HEARTBEAT_OFFLINE_TIMEOUT. | I | 1 | 24 | Input | R | 300010 | 9 | I16
RC_OfflineTimeout | 10 | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. | I | 1 | 26 | Holding | RW | 400021 | 20 | I16
RgbEnable | 0 | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | RW | 000003 | 2 | LOGIC
RgbOffColor | 0 | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | RW | 400027 | 26 | U8
RgbOffTime | 500 | Off time in ms | I | 1 | 37 | Holding | RW | 400028 | 27 | I16
RgbOnColor | 252 | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | RW | 400029 | 28 | U8
RgbOnTime | 100 | On time in ms | I | 1 | 40 | Holding | RW | 400030 | 29 | I16
product_status | 0 | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | RW | 400004 | 3 | I16
OspreyVerMajor |  | Osprey version, major part | X | 1 | 64 | Input | R | 300013 | 12 | U8
OspreyVerMinor |  | Osprey version, minor part | X | 1 | 65 | Input | R | 300014 | 13 | U8
OspreyVerBranch |  | Osprey version, branch part | X | 1 | 66 | Input | R | 300015 | 14 | U8
OspreyVerNumber |  | Osprey version, number part | X | 1 | 67 | Input | R | 300016 | 15 | U8
OspreyGitCommit |  | Osprey Git commit | I | 1 | 68 | Input | R | 300017 | 16 | I16
OsId |  | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | R | 300021 | 20 | I16
VersionNumberString |  | The application version as a string | $ | 1 | 76
gitCommitHashString |  | The Full Git hash of the application | $ | 1 | 79
BleButtonMode | 3 | Function for BLE button | X | 1 | 83 | Holding | RW | 400071 | 70 | U8
BleButtonTimeout | 120 | Timeout when BLE is started with the button | I | 1 | 84 | Holding | RW | 400072 | 71 | I16
BleVerMajor |  | BLE stack version, major part | X | 1 | 98 | Input | R | 300022 | 21 | U8
BleVerMinor |  | BLE stack version, minor part | X | 1 | 99 | Input | R | 300023 | 22 | U8
BleVerBranch |  | BLE stack version, branch part | X | 1 | 100 | Input | R | 300024 | 23 | U8
BleVerNumber |  | BLE stack version, number part | X | 1 | 101 | Input | R | 300025 | 24 | U8
FusVerMajor |  | FUS stack version, major part | X | 1 | 102 | Input | R | 300026 | 25 | U8
FusVerMinor |  | FUS version, minor part | X | 1 | 103 | Input | R | 300027 | 26 | U8
FusVerBranch |  | FUS version, branch part | X | 1 | 104 | Input | R | 300028 | 27 | U8
FusVerNumber |  | FUS version, number part | X | 1 | 105 | Input | R | 300029 | 28 | U8
RC_RoomTemp |  | Room temperature | R | 2 | 0 | Input | R | 305001 | 5000 | I16SO | 10 | 0 | analog_value | 10002 | degrees_celsius
RC_CO2Level |  | Room CO2 level | R | 2 | 3 | Input | R | 305002 | 5001 | I16SO | 1 | 0 | analog_value | 10011 | parts_per_million
RC_Humidity |  | Relative humidity | R | 2 | 21 | Input | R | 305008 | 5007 | I16SO | 10 | 0 | analog_value | 10071 | percent_relative_humidity
RC_Presence |  | Presence indication | L | 2 | 24 | Discrete | R | 105001 | 5000 | LOGIC |  |  | binary_value | 10001
RC_DIPresence |  | DI Presence indication | L | 2 | 25 | Discrete | R | 105002 | 5001 | LOGIC |  |  | binary_value | 10011
RC_CO2Presence |  | CO2 Presence indication | L | 2 | 26 | Discrete | R | 105003 | 5002 | LOGIC |  |  | binary_value | 10021
RC_VOC |  | VOC index | R | 2 | 87 | Input | R | 305033 | 5032 | I16SO | 10 | 0 | analog_value | 10281
RC_CO2Indicator |  | RGB CO2 indication | X | 2 | 96 | Input | R | 305036 | 5035 | U8 |  |  | multi_state_value | 10021
RC_CO2LevelRounded |  | Rounded room CO2 level | R | 2 | 99 | Input | R | 305037 | 5036 | I16SO | 1 | 0 | analog_value | 10311 | parts_per_million
RC_RoomTempRemote | 22 | Remote setting of room temperature | R | 3 | 318 | Holding | RW | 405210 | 5209 | I16SO | 10 | 0 | analog_value | 10611 | degrees_celsius | X
RC_CO2LevelRemote | 400 | Remote setting of room CO2 level | R | 3 | 321 | Holding | RW | 405211 | 5210 | I16SO | 10 | 0 | analog_value | 10621 | parts_per_million | X
RC_HumidityRemote | 50 | Remote setting of relative humidity | R | 3 | 339 | Holding | RW | 405217 | 5216 | I16SO | 10 | 0 | analog_value | 10681 | percent_relative_humidity | X
RC_VOCRemote | 100 | Remote setting of VOC index | R | 3 | 342 | Holding | RW | 405218 | 5217 | I16SO | 10 | 0 | analog_value | 10691 |  | X
RC_RoomTempRemoteSelect | 0 | Enable remote setting of room temperature | L | 3 | 345 | Coil | RW | 005022 | 5021 | LOGIC |  |  | binary_value | 10321 |  | X
RC_CO2LevelRemoteSelect | 0 | Enable remote setting of room CO2 level | L | 3 | 346 | Coil | RW | 005023 | 5022 | LOGIC |  |  | binary_value | 10331 |  | X
RC_HumidityRemoteSelect | 0 | Enable remote setting of relative humidity | L | 3 | 352 | Coil | RW | 005029 | 5028 | LOGIC |  |  | binary_value | 10391 |  | X
RC_VOCRemoteSelect | 0 | Enable remote setting of VOC index | L | 3 | 353 | Coil | RW | 005030 | 5029 | LOGIC |  |  | binary_value | 10401 |  | X
RC_DIPresenceRemote | 0 | Remote setting of presence digital input | L | 3 | 354 | Coil | RW | 005031 | 5030 | LOGIC |  |  | binary_value | 10411 |  | X
RC_PresenceDelayOn | 0 | Delay for presence on (min) | I | 3 | 389 | Holding | RW | 405249 | 5248 | I16
RC_PresenceDelayOff | 10 | Delay for presence off (min) | I | 3 | 391 | Holding | RW | 405250 | 5249 | I16
RC_PresenceCO2Enable | 0 | Enable CO2 presence detection | L | 3 | 393 | Coil | RW | 005036 | 5035 | LOGIC
RC_PresenceCO2Limit | 800 | CO2 presence limit | R | 3 | 394 | Holding | RW | 405251 | 5250 | I16SO | 10 | 0
RC_PresenceCO2Hyst | 160 | CO2 presence limit hysteresis | R | 3 | 397 | Holding | RW | 405252 | 5251 | I16SO | 10 | 0
RC_DIPresenceRemoteSelect | 0 | Enable remote setting of presence digital input | L | 3 | 437 | Coil | RW | 005040 | 5039 | LOGIC |  |  | binary_value | 10481 |  | X
RC_CO2FilterTime | 5 | CO2 filter time (0 to 17200 seconds) | I | 3 | 492 | Holding | RW | 405301 | 5300 | I16
RC_RHFilterTime | 5 | RH filter time (0 to 17200 seconds) | I | 3 | 494 | Holding | RW | 405302 | 5301 | I16
RC_TempFilterTime | 5 | Temperature filter time (0 to 17200 seconds) | I | 3 | 496 | Holding | RW | 405303 | 5302 | I16
IoAnaIn_1_value |  | Filtered value from sensor | R | 4 | 0 | Input | R | 301001 301002 | 1000 1001 | REGx2I32SO | 100 | 0 | analog_value | 1001
IoAnaIn_1_mode | 3 | Mode for input | X | 4 | 3 | Holding | RW | 401001 | 1000 | U8
IoAnaIn_1_unit | 0 | Unit converter | X | 4 | 4 | Holding | RW | 401002 | 1001 | U8
IoAnaIn_1_min_in | -100 | Scale for input | R | 4 | 5 | Holding | RW | 401003 401004 | 1002 1003 | REGx2I32SO | 100 | 0
IoAnaIn_1_min_out | -100 | Scale for input | R | 4 | 8 | Holding | RW | 401005 401006 | 1004 1005 | REGx2I32SO | 100 | 0
IoAnaIn_1_max_in | 10000 | Scale for input | R | 4 | 11 | Holding | RW | 401007 401008 | 1006 1007 | REGx2I32SO | 100 | 0
IoAnaIn_1_max_out | 10000 | Scale for input | R | 4 | 14 | Holding | RW | 401009 401010 | 1008 1009 | REGx2I32SO | 100 | 0
IoAnaIn_1_offset | 0 | Offset for input | R | 4 | 17 | Holding | RW | 401011 | 1010 | I16SO | 100 | 0
IoAnaIn_1_prefilter |  | Unfiltered value from sensor | R | 4 | 23 | Input | R | 301003 301004 | 1002 1003 | REGx2I32SO | 100 | 0
IoAnaIn_1_raw |  | Raw value from sensor | R | 4 | 26 | Input | R | 301005 301006 | 1004 1005 | REGx2I32SO | 100 | 0
IoAnaIn_1_override | 0 | Override value | R | 4 | 29 | Holding | RW | 401014 401015 | 1013 1014 | REGx2I32SO | 100 | 0 | analog_value | 1101 |  | X
IoAnaIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 32 | Coil | RW | 001001 | 1000 | LOGIC |  |  | binary_value | 1001 |  | X
IoAnaIn_1_error |  | Flag indicating any fault for signal | L | 4 | 33 | Discrete | R | 101001 | 1000 | LOGIC
IoAnaIn_1_errorFlags | 0 | Detailed fault description | H | 4 | 34 | Holding | RW | 401016 401017 | 1015 1016 | REGx2I32
IoAnaIn_1_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 37 | Holding | RW | 401018 | 1017 | I16
IoAnaIn_1_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 39 | Coil | RW | 001002 | 1001 | LOGIC
IoAnaIn_1_hyst | 0 | Hysteresis limit | R | 4 | 40 | Holding | RW | 401019 | 1018 | I16SO | 100 | 0
IoAnaIn_1_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 43 | Holding | RW | 401020 | 1019 | I16
IoAnaIn_1_valueDigits | 2 | Number of shown digits | I | 4 | 46 | Holding | RW | 401021 | 1020 | I16
IoAnaIn_2_value |  | Filtered value from sensor | R | 4 | 50 | Input | R | 301026 301027 | 1025 1026 | REGx2I32SO | 100 | 0 | analog_value | 1002
IoAnaIn_2_mode | 9 | Mode for input | X | 4 | 53 | Holding | RW | 401026 | 1025 | U8
IoAnaIn_2_unit | 0 | Unit converter | X | 4 | 54 | Holding | RW | 401027 | 1026 | U8
IoAnaIn_2_min_in | -100 | Scale for input | R | 4 | 55 | Holding | RW | 401028 401029 | 1027 1028 | REGx2I32SO | 100 | 0
IoAnaIn_2_min_out | -100 | Scale for input | R | 4 | 58 | Holding | RW | 401030 401031 | 1029 1030 | REGx2I32SO | 100 | 0
IoAnaIn_2_max_in | 10000 | Scale for input | R | 4 | 61 | Holding | RW | 401032 401033 | 1031 1032 | REGx2I32SO | 100 | 0
IoAnaIn_2_max_out | 10000 | Scale for input | R | 4 | 64 | Holding | RW | 401034 401035 | 1033 1034 | REGx2I32SO | 100 | 0
IoAnaIn_2_offset | 0 | Offset for input | R | 4 | 67 | Holding | RW | 401036 | 1035 | I16SO | 100 | 0
IoAnaIn_2_prefilter |  | Unfiltered value from sensor | R | 4 | 73 | Input | R | 301028 301029 | 1027 1028 | REGx2I32SO | 100 | 0
IoAnaIn_2_raw |  | Raw value from sensor | R | 4 | 76 | Input | R | 301030 301031 | 1029 1030 | REGx2I32SO | 100 | 0
IoAnaIn_2_override | 0 | Override value | R | 4 | 79 | Holding | RW | 401039 401040 | 1038 1039 | REGx2I32SO | 100 | 0 | analog_value | 1102 |  | X
IoAnaIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 82 | Coil | RW | 001026 | 1025 | LOGIC |  |  | binary_value | 1002 |  | X
IoAnaIn_2_error |  | Flag indicating any fault for signal | L | 4 | 83 | Discrete | R | 101026 | 1025 | LOGIC
IoAnaIn_2_errorFlags | 0 | Detailed fault description | H | 4 | 84 | Holding | RW | 401041 401042 | 1040 1041 | REGx2I32
IoAnaIn_2_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 87 | Holding | RW | 401043 | 1042 | I16
IoAnaIn_2_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 89 | Coil | RW | 001027 | 1026 | LOGIC
IoAnaIn_2_hyst | 0 | Hysteresis limit | R | 4 | 90 | Holding | RW | 401044 | 1043 | I16SO | 100 | 0
IoAnaIn_2_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 93 | Holding | RW | 401045 | 1044 | I16
IoAnaIn_2_valueDigits | 2 | Number of shown digits | I | 4 | 96 | Holding | RW | 401046 | 1045 | I16
IoAnaIn_3_value |  | Filtered value from sensor | R | 4 | 100 | Input | R | 301051 301052 | 1050 1051 | REGx2I32SO | 100 | 0 | analog_value | 1003
IoAnaIn_3_mode | 9 | Mode for input | X | 4 | 103 | Holding | RW | 401051 | 1050 | U8
IoAnaIn_3_unit | 0 | Unit converter | X | 4 | 104 | Holding | RW | 401052 | 1051 | U8
IoAnaIn_3_min_in | -100 | Scale for input | R | 4 | 105 | Holding | RW | 401053 401054 | 1052 1053 | REGx2I32SO | 100 | 0
IoAnaIn_3_min_out | -100 | Scale for input | R | 4 | 108 | Holding | RW | 401055 401056 | 1054 1055 | REGx2I32SO | 100 | 0
IoAnaIn_3_max_in | 10000 | Scale for input | R | 4 | 111 | Holding | RW | 401057 401058 | 1056 1057 | REGx2I32SO | 100 | 0
IoAnaIn_3_max_out | 10000 | Scale for input | R | 4 | 114 | Holding | RW | 401059 401060 | 1058 1059 | REGx2I32SO | 100 | 0
IoAnaIn_3_offset | 0 | Offset for input | R | 4 | 117 | Holding | RW | 401061 | 1060 | I16SO | 100 | 0
IoAnaIn_3_prefilter |  | Unfiltered value from sensor | R | 4 | 123 | Input | R | 301053 301054 | 1052 1053 | REGx2I32SO | 100 | 0
IoAnaIn_3_raw |  | Raw value from sensor | R | 4 | 126 | Input | R | 301055 301056 | 1054 1055 | REGx2I32SO | 100 | 0
IoAnaIn_3_override | 0 | Override value | R | 4 | 129 | Holding | RW | 401064 401065 | 1063 1064 | REGx2I32SO | 100 | 0 | analog_value | 1103 |  | X
IoAnaIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 132 | Coil | RW | 001051 | 1050 | LOGIC |  |  | binary_value | 1003 |  | X
IoAnaIn_3_error |  | Flag indicating any fault for signal | L | 4 | 133 | Discrete | R | 101051 | 1050 | LOGIC
IoAnaIn_3_errorFlags | 0 | Detailed fault description | H | 4 | 134 | Holding | RW | 401066 401067 | 1065 1066 | REGx2I32
IoAnaIn_3_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 137 | Holding | RW | 401068 | 1067 | I16
IoAnaIn_3_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 139 | Coil | RW | 001052 | 1051 | LOGIC
IoAnaIn_3_hyst | 0 | Hysteresis limit | R | 4 | 140 | Holding | RW | 401069 | 1068 | I16SO | 100 | 0
IoAnaIn_3_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 143 | Holding | RW | 401070 | 1069 | I16
IoAnaIn_4_value |  | Filtered value from sensor | R | 4 | 150 | Input | R | 301076 301077 | 1075 1076 | REGx2I32SO | 100 | 0 | analog_value | 1004
IoAnaIn_4_mode | 135 | Mode for input | X | 4 | 153 | Holding | RW | 401076 | 1075 | U8
IoAnaIn_4_unit | 0 | Unit converter | X | 4 | 154 | Holding | RW | 401077 | 1076 | U8
IoAnaIn_4_min_in | -100 | Scale for input | R | 4 | 155 | Holding | RW | 401078 401079 | 1077 1078 | REGx2I32SO | 100 | 0
IoAnaIn_4_min_out | -100 | Scale for input | R | 4 | 158 | Holding | RW | 401080 401081 | 1079 1080 | REGx2I32SO | 100 | 0
IoAnaIn_4_max_in | 10000 | Scale for input | R | 4 | 161 | Holding | RW | 401082 401083 | 1081 1082 | REGx2I32SO | 100 | 0
IoAnaIn_4_max_out | 10000 | Scale for input | R | 4 | 164 | Holding | RW | 401084 401085 | 1083 1084 | REGx2I32SO | 100 | 0
IoAnaIn_4_offset | 0 | Offset for input | R | 4 | 167 | Holding | RW | 401086 | 1085 | I16SO | 100 | 0
IoAnaIn_4_prefilter |  | Unfiltered value from sensor | R | 4 | 173 | Input | R | 301078 301079 | 1077 1078 | REGx2I32SO | 100 | 0
IoAnaIn_4_raw |  | Raw value from sensor | R | 4 | 176 | Input | R | 301080 301081 | 1079 1080 | REGx2I32SO | 100 | 0
IoAnaIn_4_override | 0 | Override value | R | 4 | 179 | Holding | RW | 401089 401090 | 1088 1089 | REGx2I32SO | 100 | 0 | analog_value | 1104 |  | X
IoAnaIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 182 | Coil | RW | 001076 | 1075 | LOGIC |  |  | binary_value | 1004 |  | X
IoAnaIn_4_error |  | Flag indicating any fault for signal | L | 4 | 183 | Discrete | R | 101076 | 1075 | LOGIC
IoAnaIn_4_errorFlags | 0 | Detailed fault description | H | 4 | 184 | Holding | RW | 401091 401092 | 1090 1091 | REGx2I32
IoAnaIn_4_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 187 | Holding | RW | 401093 | 1092 | I16
IoAnaIn_4_hyst | 0 | Hysteresis limit | R | 4 | 190 | Holding | RW | 401094 | 1093 | I16SO | 100 | 0
IoAnaIn_4_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 193 | Holding | RW | 401095 | 1094 | I16
IoAnaIn_5_value |  | Filtered value from sensor | R | 4 | 200 | Input | R | 301101 301102 | 1100 1101 | REGx2I32SO | 100 | 0 | analog_value | 1005
IoAnaIn_5_mode | 128 | Room Temperature sensor mode | X | 4 | 203 | Holding | RW | 401101 | 1100 | U8
IoAnaIn_5_unit | 0 | Unit converter | X | 4 | 204 | Holding | RW | 401102 | 1101 | U8
IoAnaIn_5_min_in | -10 | Room Temperature Min Input | R | 4 | 205 | Holding | RW | 401103 401104 | 1102 1103 | REGx2I32SO | 100 | 0
IoAnaIn_5_min_out | -10 | Room Temperature Min Output | R | 4 | 208 | Holding | RW | 401105 401106 | 1104 1105 | REGx2I32SO | 100 | 0
IoAnaIn_5_max_in | 60 | Room Temperature Max Input | R | 4 | 211 | Holding | RW | 401107 401108 | 1106 1107 | REGx2I32SO | 100 | 0
IoAnaIn_5_max_out | 60 | Room Temperature Max Output | R | 4 | 214 | Holding | RW | 401109 401110 | 1108 1109 | REGx2I32SO | 100 | 0
IoAnaIn_5_offset | 0 | Offset for input | R | 4 | 217 | Holding | RW | 401111 | 1110 | I16SO | 100 | 0
IoAnaIn_5_prefilter |  | Unfiltered value from sensor | R | 4 | 223 | Input | R | 301103 301104 | 1102 1103 | REGx2I32SO | 100 | 0
IoAnaIn_5_raw |  | Raw value from sensor | R | 4 | 226 | Input | R | 301105 301106 | 1104 1105 | REGx2I32SO | 100 | 0
IoAnaIn_5_override | 0 | Override value | R | 4 | 229 | Holding | RW | 401114 401115 | 1113 1114 | REGx2I32SO | 100 | 0 | analog_value | 1105 |  | X
IoAnaIn_5_override_en | 0 | Set to 1 to enable override | L | 4 | 232 | Coil | RW | 001101 | 1100 | LOGIC |  |  | binary_value | 1005 |  | X
IoAnaIn_5_error |  | Flag indicating any fault for signal | L | 4 | 233 | Discrete | R | 101101 | 1100 | LOGIC
IoAnaIn_5_errorFlags | 0 | Detailed fault description | H | 4 | 234 | Holding | RW | 401116 401117 | 1115 1116 | REGx2I32
IoAnaIn_5_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 237 | Holding | RW | 401118 | 1117 | I16
IoAnaIn_5_limit | 1 | Room Temperature Limit at min/max | L | 4 | 239 | Coil | RW | 001102 | 1101 | LOGIC
IoAnaIn_5_hyst | 0 | Hysteresis limit | R | 4 | 240 | Holding | RW | 401119 | 1118 | I16SO | 100 | 0
IoAnaIn_6_value |  | Filtered value from sensor | R | 4 | 250 | Input | R | 301126 301127 | 1125 1126 | REGx2I32SO | 100 | 0 | analog_value | 1006
IoAnaIn_6_mode | 128 | Room Humidity sensor mode | X | 4 | 253 | Holding | RW | 401126 | 1125 | U8
IoAnaIn_6_unit | 0 | Unit converter | X | 4 | 254 | Holding | RW | 401127 | 1126 | U8
IoAnaIn_6_min_in | 0 | Room Humidity Min Input | R | 4 | 255 | Holding | RW | 401128 401129 | 1127 1128 | REGx2I32SO | 100 | 0
IoAnaIn_6_min_out | 0 | Room Humidity Min Output | R | 4 | 258 | Holding | RW | 401130 401131 | 1129 1130 | REGx2I32SO | 100 | 0
IoAnaIn_6_max_in | 100 | Room Humidity Max Input | R | 4 | 261 | Holding | RW | 401132 401133 | 1131 1132 | REGx2I32SO | 100 | 0
IoAnaIn_6_max_out | 100 | Room Humidity Max Output | R | 4 | 264 | Holding | RW | 401134 401135 | 1133 1134 | REGx2I32SO | 100 | 0
IoAnaIn_6_offset | 0 | Offset for input | R | 4 | 267 | Holding | RW | 401136 | 1135 | I16SO | 100 | 0
IoAnaIn_6_prefilter |  | Unfiltered value from sensor | R | 4 | 273 | Input | R | 301128 301129 | 1127 1128 | REGx2I32SO | 100 | 0
IoAnaIn_6_raw |  | Raw value from sensor | R | 4 | 276 | Input | R | 301130 301131 | 1129 1130 | REGx2I32SO | 100 | 0
IoAnaIn_6_override | 0 | Override value | R | 4 | 279 | Holding | RW | 401139 401140 | 1138 1139 | REGx2I32SO | 100 | 0 | analog_value | 1106 |  | X
IoAnaIn_6_override_en | 0 | Set to 1 to enable override | L | 4 | 282 | Coil | RW | 001126 | 1125 | LOGIC |  |  | binary_value | 1006 |  | X
IoAnaIn_6_error |  | Flag indicating any fault for signal | L | 4 | 283 | Discrete | R | 101126 | 1125 | LOGIC
IoAnaIn_6_errorFlags | 0 | Detailed fault description | H | 4 | 284 | Holding | RW | 401141 401142 | 1140 1141 | REGx2I32
IoAnaIn_6_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 287 | Holding | RW | 401143 | 1142 | I16
IoAnaIn_6_limit | 1 | Room Humidity Limit at min/max | L | 4 | 289 | Coil | RW | 001127 | 1126 | LOGIC
IoAnaIn_6_hyst | 0 | Hysteresis limit | R | 4 | 290 | Holding | RW | 401144 | 1143 | I16SO | 100 | 0
IoAnaIn_7_value |  | Filtered value from sensor | R | 4 | 300 | Input | R | 301151 301152 | 1150 1151 | REGx2I32SO | 100 | 0 | analog_value | 1007
IoAnaIn_7_mode | 128 | Room VOC sensor mode | X | 4 | 303 | Holding | RW | 401151 | 1150 | U8
IoAnaIn_7_unit | 0 | Unit converter | X | 4 | 304 | Holding | RW | 401152 | 1151 | U8
IoAnaIn_7_min_in | 0 | Room VOC Min Input | R | 4 | 305 | Holding | RW | 401153 401154 | 1152 1153 | REGx2I32SO | 100 | 0
IoAnaIn_7_min_out | 0 | Room VOC Min Output | R | 4 | 308 | Holding | RW | 401155 401156 | 1154 1155 | REGx2I32SO | 100 | 0
IoAnaIn_7_max_in | 500 | Room VOC Max Input | R | 4 | 311 | Holding | RW | 401157 401158 | 1156 1157 | REGx2I32SO | 100 | 0
IoAnaIn_7_max_out | 500 | Room VOC Max Output | R | 4 | 314 | Holding | RW | 401159 401160 | 1158 1159 | REGx2I32SO | 100 | 0
IoAnaIn_7_offset | 0 | Offset for input | R | 4 | 317 | Holding | RW | 401161 | 1160 | I16SO | 100 | 0
IoAnaIn_7_prefilter |  | Unfiltered value from sensor | R | 4 | 323 | Input | R | 301153 301154 | 1152 1153 | REGx2I32SO | 100 | 0
IoAnaIn_7_raw |  | Raw value from sensor | R | 4 | 326 | Input | R | 301155 301156 | 1154 1155 | REGx2I32SO | 100 | 0
IoAnaIn_7_override | 0 | Override value | R | 4 | 329 | Holding | RW | 401164 401165 | 1163 1164 | REGx2I32SO | 100 | 0 | analog_value | 1107 |  | X
IoAnaIn_7_override_en | 0 | Set to 1 to enable override | L | 4 | 332 | Coil | RW | 001151 | 1150 | LOGIC |  |  | binary_value | 1007 |  | X
IoAnaIn_7_error |  | Flag indicating any fault for signal | L | 4 | 333 | Discrete | R | 101151 | 1150 | LOGIC
IoAnaIn_7_errorFlags | 0 | Detailed fault description | H | 4 | 334 | Holding | RW | 401166 401167 | 1165 1166 | REGx2I32
IoAnaIn_7_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 337 | Holding | RW | 401168 | 1167 | I16
IoAnaIn_7_limit | 1 | Room VOC Limit at min/max | L | 4 | 339 | Coil | RW | 001152 | 1151 | LOGIC
IoAnaIn_7_hyst | 0 | Hysteresis limit | R | 4 | 340 | Holding | RW | 401169 | 1168 | I16SO | 100 | 0
IoAnaIn_8_value |  | Filtered value from sensor | R | 4 | 350 | Input | R | 301176 301177 | 1175 1176 | REGx2I32SO | 100 | 0 | analog_value | 1008
IoAnaIn_8_mode | 128 | Room CO2 sensor mode | X | 4 | 353 | Holding | RW | 401176 | 1175 | U8
IoAnaIn_8_unit | 0 | Unit converter | X | 4 | 354 | Holding | RW | 401177 | 1176 | U8
IoAnaIn_8_min_in | 400 | Room CO2 Min Input | R | 4 | 355 | Holding | RW | 401178 401179 | 1177 1178 | REGx2I32SO | 100 | 0
IoAnaIn_8_min_out | 400 | Room CO2 Min Output | R | 4 | 358 | Holding | RW | 401180 401181 | 1179 1180 | REGx2I32SO | 100 | 0
IoAnaIn_8_max_in | 2000 | Room CO2 Max Input | R | 4 | 361 | Holding | RW | 401182 401183 | 1181 1182 | REGx2I32SO | 100 | 0
IoAnaIn_8_max_out | 2000 | Room CO2 Max Output | R | 4 | 364 | Holding | RW | 401184 401185 | 1183 1184 | REGx2I32SO | 100 | 0
IoAnaIn_8_offset | 0 | Offset for input | R | 4 | 367 | Holding | RW | 401186 | 1185 | I16SO | 100 | 0
IoAnaIn_8_prefilter |  | Unfiltered value from sensor | R | 4 | 373 | Input | R | 301178 301179 | 1177 1178 | REGx2I32SO | 100 | 0
IoAnaIn_8_raw |  | Raw value from sensor | R | 4 | 376 | Input | R | 301180 301181 | 1179 1180 | REGx2I32SO | 100 | 0
IoAnaIn_8_override | 0 | Override value | R | 4 | 379 | Holding | RW | 401189 401190 | 1188 1189 | REGx2I32SO | 100 | 0 | analog_value | 1108 |  | X
IoAnaIn_8_override_en | 0 | Set to 1 to enable override | L | 4 | 382 | Coil | RW | 001176 | 1175 | LOGIC |  |  | binary_value | 1008 |  | X
IoAnaIn_8_error |  | Flag indicating any fault for signal | L | 4 | 383 | Discrete | R | 101176 | 1175 | LOGIC
IoAnaIn_8_errorFlags | 0 | Detailed fault description | H | 4 | 384 | Holding | RW | 401191 401192 | 1190 1191 | REGx2I32
IoAnaIn_8_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 387 | Holding | RW | 401193 | 1192 | I16
IoAnaIn_8_limit | 1 | Room CO2 Limit at min/max | L | 4 | 389 | Coil | RW | 001177 | 1176 | LOGIC
IoAnaIn_8_hyst | 0 | Hysteresis limit | R | 4 | 390 | Holding | RW | 401194 | 1193 | I16SO | 100 | 0
IoAnaIn_8_valueDigits | 2 | Number of shown digits | I | 4 | 396 | Holding | RW | 401196 | 1195 | I16
IoAnaIn_9_value |  | Filtered value from sensor | R | 4 | 400 | Input | R | 301201 301202 | 1200 1201 | REGx2I32SO | 100 | 0 | analog_value | 1009
IoAnaIn_9_mode | 9 | Mode for input | X | 4 | 403 | Holding | RW | 401201 | 1200 | U8
IoAnaIn_9_unit | 0 | Unit converter | X | 4 | 404 | Holding | RW | 401202 | 1201 | U8
IoAnaIn_9_min_in | -100 | Scale for input | R | 4 | 405 | Holding | RW | 401203 401204 | 1202 1203 | REGx2I32SO | 100 | 0
IoAnaIn_9_min_out | -100 | Scale for input | R | 4 | 408 | Holding | RW | 401205 401206 | 1204 1205 | REGx2I32SO | 100 | 0
IoAnaIn_9_max_in | 10000 | Scale for input | R | 4 | 411 | Holding | RW | 401207 401208 | 1206 1207 | REGx2I32SO | 100 | 0
IoAnaIn_9_max_out | 10000 | Scale for input | R | 4 | 414 | Holding | RW | 401209 401210 | 1208 1209 | REGx2I32SO | 100 | 0
IoAnaIn_9_offset | 0 | Offset for input | R | 4 | 417 | Holding | RW | 401211 | 1210 | I16SO | 100 | 0
IoAnaIn_9_prefilter |  | Unfiltered value from sensor | R | 4 | 423 | Input | R | 301203 301204 | 1202 1203 | REGx2I32SO | 100 | 0
IoAnaIn_9_raw |  | Raw value from sensor | R | 4 | 426 | Input | R | 301205 301206 | 1204 1205 | REGx2I32SO | 100 | 0
IoAnaIn_9_override | 0 | Override value | R | 4 | 429 | Holding | RW | 401214 401215 | 1213 1214 | REGx2I32SO | 100 | 0 | analog_value | 1109 |  | X
IoAnaIn_9_override_en | 0 | Set to 1 to enable override | L | 4 | 432 | Coil | RW | 001201 | 1200 | LOGIC |  |  | binary_value | 1009 |  | X
IoAnaIn_9_error |  | Flag indicating any fault for signal | L | 4 | 433 | Discrete | R | 101201 | 1200 | LOGIC
IoAnaIn_9_errorFlags | 0 | Detailed fault description | H | 4 | 434 | Holding | RW | 401216 401217 | 1215 1216 | REGx2I32
IoAnaIn_9_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 437 | Holding | RW | 401218 | 1217 | I16
IoAnaIn_9_hyst | 0 | Hysteresis limit | R | 4 | 440 | Holding | RW | 401219 | 1218 | I16SO | 100 | 0
IoAnaIn_10_value |  | Filtered value from sensor | R | 4 | 450 | Input | R | 301226 301227 | 1225 1226 | REGx2I32SO | 100 | 0 | analog_value | 1010
IoAnaIn_10_mode | 128 | Mode for input | X | 4 | 453 | Holding | RW | 401226 | 1225 | U8
IoAnaIn_10_unit | 0 | Unit converter | X | 4 | 454 | Holding | RW | 401227 | 1226 | U8
IoAnaIn_10_min_in | -100 | Scale for input | R | 4 | 455 | Holding | RW | 401228 401229 | 1227 1228 | REGx2I32SO | 100 | 0
IoAnaIn_10_min_out | -100 | Scale for input | R | 4 | 458 | Holding | RW | 401230 401231 | 1229 1230 | REGx2I32SO | 100 | 0
IoAnaIn_10_max_in | 10000 | Scale for input | R | 4 | 461 | Holding | RW | 401232 401233 | 1231 1232 | REGx2I32SO | 100 | 0
IoAnaIn_10_max_out | 10000 | Scale for input | R | 4 | 464 | Holding | RW | 401234 401235 | 1233 1234 | REGx2I32SO | 100 | 0
IoAnaIn_10_offset | 0 | Offset for input | R | 4 | 467 | Holding | RW | 401236 | 1235 | I16SO | 100 | 0
IoAnaIn_10_prefilter |  | Unfiltered value from sensor | R | 4 | 473 | Input | R | 301228 301229 | 1227 1228 | REGx2I32SO | 100 | 0
IoAnaIn_10_raw |  | Raw value from sensor | R | 4 | 476 | Input | R | 301230 301231 | 1229 1230 | REGx2I32SO | 100 | 0
IoAnaIn_10_override | 0 | Override value | R | 4 | 479 | Holding | RW | 401239 401240 | 1238 1239 | REGx2I32SO | 100 | 0 | analog_value | 1110 |  | X
IoAnaIn_10_override_en | 0 | Set to 1 to enable override | L | 4 | 482 | Coil | RW | 001226 | 1225 | LOGIC |  |  | binary_value | 1010 |  | X
IoAnaIn_10_error |  | Flag indicating any fault for signal | L | 4 | 483 | Discrete | R | 101226 | 1225 | LOGIC
IoAnaIn_10_errorFlags | 0 | Detailed fault description | H | 4 | 484 | Holding | RW | 401241 401242 | 1240 1241 | REGx2I32
IoAnaIn_10_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 487 | Holding | RW | 401243 | 1242 | I16
IoAnaIn_10_hyst | 0 | Hysteresis limit | R | 4 | 490 | Holding | RW | 401244 | 1243 | I16SO | 100 | 0
IoAnaIn_11_value |  | Filtered value from sensor | R | 4 | 500 | Input | R | 301251 301252 | 1250 1251 | REGx2I32SO | 100 | 0 | analog_value | 1011
IoAnaIn_11_mode | 128 | Mode for input | X | 4 | 503 | Holding | RW | 401251 | 1250 | U8
IoAnaIn_11_unit | 0 | Unit converter | X | 4 | 504 | Holding | RW | 401252 | 1251 | U8
IoAnaIn_11_min_in | -100 | Scale for input | R | 4 | 505 | Holding | RW | 401253 401254 | 1252 1253 | REGx2I32SO | 100 | 0
IoAnaIn_11_min_out | -100 | Scale for input | R | 4 | 508 | Holding | RW | 401255 401256 | 1254 1255 | REGx2I32SO | 100 | 0
IoAnaIn_11_max_in | 10000 | Scale for input | R | 4 | 511 | Holding | RW | 401257 401258 | 1256 1257 | REGx2I32SO | 100 | 0
IoAnaIn_11_max_out | 10000 | Scale for input | R | 4 | 514 | Holding | RW | 401259 401260 | 1258 1259 | REGx2I32SO | 100 | 0
IoAnaIn_11_offset | 0 | Offset for input | R | 4 | 517 | Holding | RW | 401261 | 1260 | I16SO | 100 | 0
IoAnaIn_11_prefilter |  | Unfiltered value from sensor | R | 4 | 523 | Input | R | 301253 301254 | 1252 1253 | REGx2I32SO | 100 | 0
IoAnaIn_11_raw |  | Raw value from sensor | R | 4 | 526 | Input | R | 301255 301256 | 1254 1255 | REGx2I32SO | 100 | 0
IoAnaIn_11_override | 0 | Override value | R | 4 | 529 | Holding | RW | 401264 401265 | 1263 1264 | REGx2I32SO | 100 | 0 | analog_value | 1111 |  | X
IoAnaIn_11_override_en | 0 | Set to 1 to enable override | L | 4 | 532 | Coil | RW | 001251 | 1250 | LOGIC |  |  | binary_value | 1011 |  | X
IoAnaIn_11_error |  | Flag indicating any fault for signal | L | 4 | 533 | Discrete | R | 101251 | 1250 | LOGIC
IoAnaIn_11_errorFlags | 0 | Detailed fault description | H | 4 | 534 | Holding | RW | 401266 401267 | 1265 1266 | REGx2I32
IoAnaIn_11_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 537 | Holding | RW | 401268 | 1267 | I16
IoAnaIn_11_hyst | 0 | Hysteresis limit | R | 4 | 540 | Holding | RW | 401269 | 1268 | I16SO | 100 | 0
IoAnaIn_11_valueDigits | 2 | Number of shown digits | I | 4 | 546 | Holding | RW | 401271 | 1270 | I16
IoDiIn_1_value |  | Filtered value from sensor | L | 4 | 1000 | Discrete | R | 101501 | 1500 | LOGIC |  |  | binary_value | 1101
IoDiIn_1_mode | 130 | Mode for input | X | 4 | 1001 | Holding | RW | 401501 | 1500 | U8
IoDiIn_1_invert | 1 | Invert logic signal | L | 4 | 1002 | Coil | RW | 001501 | 1500 | LOGIC
IoDiIn_1_limit | 900 | Limit for analog value | R | 4 | 1003 | Holding | RW | 401502 | 1501 | I16SO | 20 | 0
IoDiIn_1_pulse1 | 0 | Pulse counter 1 | H | 4 | 1006 | Holding | RW | 401503 401504 | 1502 1503 | REGx2I32 |  |  | positive_integer_value | 10000
IoDiIn_1_pulse2 | 0 | Pulse counter 2 | H | 4 | 1009 | Holding | RW | 401505 401506 | 1504 1505 | REGx2I32 |  |  | positive_integer_value | 10002
IoDiIn_1_pulserate | 0 | Pulse rate in Hz | R | 4 | 1012 | Holding | RW | 401507 | 1506 | I16SO | 100 | 0 | analog_value | 10000 | hertz
IoDiIn_1_override | 0 | Override value | L | 4 | 1016 | Coil | RW | 001503 | 1502 | LOGIC |  |  | binary_value | 1201 |  | X
IoDiIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 1017 | Coil | RW | 001504 | 1503 | LOGIC |  |  | binary_value | 1301 |  | X
IoDiIn_1_hyst | 10 | Hysteresis limit | X | 4 | 1022 | Holding | RW | 401510 | 1509 | U8
IoDiIn_2_value |  | Filtered value from sensor | L | 4 | 1050 | Discrete | R | 101526 | 1525 | LOGIC |  |  | binary_value | 1102
IoDiIn_2_mode | 130 | Mode for input | X | 4 | 1051 | Holding | RW | 401526 | 1525 | U8
IoDiIn_2_invert | 1 | Invert logic signal | L | 4 | 1052 | Coil | RW | 001526 | 1525 | LOGIC
IoDiIn_2_limit |  | Limit for analog value | R | 4 | 1053 | Holding | RW | 401527 | 1526 | I16SO | 20 | 0
IoDiIn_2_pulse1 | 0 | Pulse counter 1 | H | 4 | 1056 | Holding | RW | 401528 401529 | 1527 1528 | REGx2I32 |  |  | positive_integer_value | 10001
IoDiIn_2_pulse2 | 0 | Pulse counter 2 | H | 4 | 1059 | Holding | RW | 401530 401531 | 1529 1530 | REGx2I32 |  |  | positive_integer_value | 10003
IoDiIn_2_pulserate | 0 | Pulse rate in Hz | R | 4 | 1062 | Holding | RW | 401532 | 1531 | I16SO | 100 | 0 | analog_value | 10001 | hertz
IoDiIn_2_override | 0 | Override value | L | 4 | 1066 | Coil | RW | 001528 | 1527 | LOGIC |  |  | binary_value | 1202 |  | X
IoDiIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 1067 | Coil | RW | 001529 | 1528 | LOGIC |  |  | binary_value | 1302 |  | X
IoDiIn_2_hyst | 10 | Hysteresis limit | X | 4 | 1072 | Holding | RW | 401535 | 1534 | U8
IoDiIn_3_value |  | Filtered value from sensor | L | 4 | 1100 | Discrete | R | 101551 | 1550 | LOGIC |  |  | binary_value | 1103
IoDiIn_3_mode | 130 | Mode for input | X | 4 | 1101 | Holding | RW | 401551 | 1550 | U8
IoDiIn_3_invert | 1 | Invert logic signal | L | 4 | 1102 | Coil | RW | 001551 | 1550 | LOGIC
IoDiIn_3_limit | 180 | Limit for analog value | R | 4 | 1103 | Holding | RW | 401552 | 1551 | I16SO | 20 | 0
IoDiIn_3_pulse1 | 0 | Pulse counter 1 | H | 4 | 1106 | Holding | RW | 401553 401554 | 1552 1553 | REGx2I32 |  |  | positive_integer_value
IoDiIn_3_pulse2 | 0 | Pulse counter 2 | H | 4 | 1109 | Holding | RW | 401555 401556 | 1554 1555 | REGx2I32 |  |  | positive_integer_value
IoDiIn_3_pulserate | 0 | Pulse rate in Hz | R | 4 | 1112 | Holding | RW | 401557 | 1556 | I16SO | 100 | 0 | analog_value
IoDiIn_3_override | 0 | Override value | L | 4 | 1116 | Coil | RW | 001553 | 1552 | LOGIC |  |  | binary_value | 1203 |  | X
IoDiIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 1117 | Coil | RW | 001554 | 1553 | LOGIC |  |  | binary_value | 1303 |  | X
IoDiIn_3_hyst | 10 | Hysteresis limit | X | 4 | 1122 | Holding | RW | 401560 | 1559 | U8
IoDiIn_4_value |  | Filtered value from sensor | L | 4 | 1150 | Discrete | R | 101576 | 1575 | LOGIC |  |  | binary_value | 1104
IoDiIn_4_mode | 130 | Mode for input | X | 4 | 1151 | Holding | RW | 401576 | 1575 | U8
IoDiIn_4_invert | 0 | Invert logic signal | L | 4 | 1152 | Coil | RW | 001576 | 1575 | LOGIC
IoDiIn_4_pulse1 | 0 | Pulse counter 1 | H | 4 | 1156 | Holding | RW | 401578 401579 | 1577 1578 | REGx2I32 |  |  | positive_integer_value
IoDiIn_4_pulse2 | 0 | Pulse counter 2 | H | 4 | 1159 | Holding | RW | 401580 401581 | 1579 1580 | REGx2I32 |  |  | positive_integer_value
IoDiIn_4_pulserate | 0 | Pulse rate in Hz | R | 4 | 1162 | Holding | RW | 401582 | 1581 | I16SO | 100 | 0 | analog_value
IoDiIn_4_override | 0 | Override value | L | 4 | 1166 | Coil | RW | 001578 | 1577 | LOGIC |  |  | binary_value | 1204 |  | X
IoDiIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 1167 | Coil | RW | 001579 | 1578 | LOGIC |  |  | binary_value | 1304 |  | X
IoAnaOut_1_value | 0 | Value in % set for output | R | 5 | 0 | Holding | RW | 402501 | 2500 | I16SO | 100 | 0 | analog_value | 1201 | percent | X
IoAnaOut_1_mode | 1 | Mode for output | X | 5 | 3 | Holding | RW | 402502 | 2501 | U8
IoAnaOut_1_unit | 0 | Unit converter | X | 5 | 4 | Holding | RW | 402503 | 2502 | U8
IoAnaOut_1_min_in | 0 | Scale for output | R | 5 | 5 | Holding | RW | 402504 | 2503 | I16SO | 100 | 0
IoAnaOut_1_min_out | 0 | Scale for output | R | 5 | 8 | Holding | RW | 402505 | 2504 | I16SO | 100 | 0
IoAnaOut_1_max_in | 100 | Scale for output | R | 5 | 11 | Holding | RW | 402506 | 2505 | I16SO | 100 | 0
IoAnaOut_1_max_out | 100 | Scale for output | R | 5 | 14 | Holding | RW | 402507 | 2506 | I16SO | 100 | 0
IoAnaOut_1_offset | 0 | Offset for output | R | 5 | 17 | Holding | RW | 402508 | 2507 | I16SO | 100 | 0
IoAnaOut_1_default | 0 | Default value if communication is lost | R | 5 | 20 | Holding | RW | 402509 | 2508 | I16SO | 100 | 0 | analog_value | 1301 | percent | X
IoAnaOut_1_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 23 | Input | R | 302501 | 2500 | I16SO | 100 | 0 | analog_value | 1401 | volts
IoAnaOut_1_raw |  | Raw value sent to HW | R | 5 | 26 | Input | R | 302502 | 2501 | I16SO | 100 | 0
IoAnaOut_1_override | 0 | Override value | R | 5 | 29 | Holding | RW | 402510 | 2509 | I16SO | 100 | 0 | analog_value | 1501 | percent | X
IoAnaOut_1_override_en | 0 | Set to 1 to enable override | L | 5 | 32 | Coil | RW | 002501 | 2500 | LOGIC |  |  | binary_value | 1401 |  | X
IoAnaOut_1_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 33 | Holding | RW | 402511 | 2510 | I16SO | 100 | 0
IoAnaOut_1_pulse_period | 60 | Period time for pulse output | I | 5 | 36 | Holding | RW | 402512 | 2511 | I16
IoAnaOut_2_value | 0 | Value in % set for output | R | 5 | 50 | Holding | RW | 402526 | 2525 | I16SO | 100 | 0 | analog_value | 1202 | percent | X
IoAnaOut_2_mode | 1 | Mode for output | X | 5 | 53 | Holding | RW | 402527 | 2526 | U8
IoAnaOut_2_unit | 0 | Unit converter | X | 5 | 54 | Holding | RW | 402528 | 2527 | U8
IoAnaOut_2_min_in | 0 | Scale for output | R | 5 | 55 | Holding | RW | 402529 | 2528 | I16SO | 100 | 0
IoAnaOut_2_min_out | 0 | Scale for output | R | 5 | 58 | Holding | RW | 402530 | 2529 | I16SO | 100 | 0
IoAnaOut_2_max_in | 100 | Scale for output | R | 5 | 61 | Holding | RW | 402531 | 2530 | I16SO | 100 | 0
IoAnaOut_2_max_out | 100 | Scale for output | R | 5 | 64 | Holding | RW | 402532 | 2531 | I16SO | 100 | 0
IoAnaOut_2_offset | 0 | Offset for output | R | 5 | 67 | Holding | RW | 402533 | 2532 | I16SO | 100 | 0
IoAnaOut_2_default | 0 | Default value if communication is lost | R | 5 | 70 | Holding | RW | 402534 | 2533 | I16SO | 100 | 0 | analog_value | 1302 | percent | X
IoAnaOut_2_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 73 | Input | R | 302526 | 2525 | I16SO | 100 | 0 | analog_value | 1402 | volts
IoAnaOut_2_raw |  | Raw value sent to HW | R | 5 | 76 | Input | R | 302527 | 2526 | I16SO | 100 | 0
IoAnaOut_2_override | 0 | Override value | R | 5 | 79 | Holding | RW | 402535 | 2534 | I16SO | 100 | 0 | analog_value | 1502 | percent | X
IoAnaOut_2_override_en | 0 | Set to 1 to enable override | L | 5 | 82 | Coil | RW | 002526 | 2525 | LOGIC |  |  | binary_value | 1402 |  | X
IoAnaOut_2_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 83 | Holding | RW | 402536 | 2535 | I16SO | 100 | 0
IoAnaOut_2_pulse_period | 60 | Period time for pulse output | I | 5 | 86 | Holding | RW | 402537 | 2536 | I16
IoAnaOut_3_value | 0 | Value in % set for output | R | 5 | 100 | Holding | RW | 402551 | 2550 | I16SO | 100 | 0 | analog_value | 1203 | percent | X
IoAnaOut_3_mode | 1 | Mode for output | X | 5 | 103 | Holding | RW | 402552 | 2551 | U8
IoAnaOut_3_unit | 0 | Unit converter | X | 5 | 104 | Holding | RW | 402553 | 2552 | U8
IoAnaOut_3_min_in | 0 | Scale for output | R | 5 | 105 | Holding | RW | 402554 | 2553 | I16SO | 100 | 0
IoAnaOut_3_min_out | 0 | Scale for output | R | 5 | 108 | Holding | RW | 402555 | 2554 | I16SO | 100 | 0
IoAnaOut_3_max_in | 100 | Scale for output | R | 5 | 111 | Holding | RW | 402556 | 2555 | I16SO | 100 | 0
IoAnaOut_3_max_out | 100 | Scale for output | R | 5 | 114 | Holding | RW | 402557 | 2556 | I16SO | 100 | 0
IoAnaOut_3_offset | 0 | Offset for output | R | 5 | 117 | Holding | RW | 402558 | 2557 | I16SO | 100 | 0
IoAnaOut_3_default | 0 | Default value if communication is lost | R | 5 | 120 | Holding | RW | 402559 | 2558 | I16SO | 100 | 0 | analog_value | 1303 | percent | X
IoAnaOut_3_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 123 | Input | R | 302551 | 2550 | I16SO | 100 | 0 | analog_value | 1403 | volts
IoAnaOut_3_raw |  | Raw value sent to HW | R | 5 | 126 | Input | R | 302552 | 2551 | I16SO | 100 | 0
IoAnaOut_3_override | 0 | Override value | R | 5 | 129 | Holding | RW | 402560 | 2559 | I16SO | 100 | 0 | analog_value | 1503 | percent | X
IoAnaOut_3_override_en | 0 | Set to 1 to enable override | L | 5 | 132 | Coil | RW | 002551 | 2550 | LOGIC |  |  | binary_value | 1403 |  | X
IoAnaOut_3_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 133 | Holding | RW | 402561 | 2560 | I16SO | 100 | 0
IoAnaOut_3_pulse_period | 60 | Period time for pulse output | I | 5 | 136 | Holding | RW | 402562 | 2561 | I16
IoAnaOut_4_value | 0 | Value in % set for output | R | 5 | 150 | Holding | RW | 402576 | 2575 | I16SO | 100 | 0 | analog_value | 1204 | percent | X
IoAnaOut_4_mode | 1 | Mode for output | X | 5 | 153 | Holding | RW | 402577 | 2576 | U8
IoAnaOut_4_unit | 0 | Unit converter | X | 5 | 154 | Holding | RW | 402578 | 2577 | U8
IoAnaOut_4_min_in | 0 | Scale for output | R | 5 | 155 | Holding | RW | 402579 | 2578 | I16SO | 100 | 0
IoAnaOut_4_min_out | 0 | Scale for output | R | 5 | 158 | Holding | RW | 402580 | 2579 | I16SO | 100 | 0
IoAnaOut_4_max_in | 100 | Scale for output | R | 5 | 161 | Holding | RW | 402581 | 2580 | I16SO | 100 | 0
IoAnaOut_4_max_out | 100 | Scale for output | R | 5 | 164 | Holding | RW | 402582 | 2581 | I16SO | 100 | 0
IoAnaOut_4_offset | 0 | Offset for output | R | 5 | 167 | Holding | RW | 402583 | 2582 | I16SO | 100 | 0
IoAnaOut_4_default | 0 | Default value if communication is lost | R | 5 | 170 | Holding | RW | 402584 | 2583 | I16SO | 100 | 0 | analog_value | 1304 | percent | X
IoAnaOut_4_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 173 | Input | R | 302576 | 2575 | I16SO | 100 | 0 | analog_value | 1404 | volts
IoAnaOut_4_raw |  | Raw value sent to HW | R | 5 | 176 | Input | R | 302577 | 2576 | I16SO | 100 | 0
IoAnaOut_4_override | 0 | Override value | R | 5 | 179 | Holding | RW | 402585 | 2584 | I16SO | 100 | 0 | analog_value | 1504 | percent | X
IoAnaOut_4_override_en | 0 | Set to 1 to enable override | L | 5 | 182 | Coil | RW | 002576 | 2575 | LOGIC |  |  | binary_value | 1404 |  | X
IoAnaOut_4_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 183 | Holding | RW | 402586 | 2585 | I16SO | 100 | 0
IoAnaOut_4_pulse_period | 60 | Period time for pulse output | I | 5 | 186 | Holding | RW | 402587 | 2586 | I16
Disp_BrightnessFull | 100 | Display brightness, full (%) | X | 6 | 0 | Holding | RW | 406001 | 6000 | U8 |  |  | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | Display brightness, dimmed (%) | X | 6 | 1 | Holding | RW | 406002 | 6001 | U8 |  |  | analog_value | 8011 | percent | X
Disp_TimeFull | 30 | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | RW | 406003 | 6002 | I16 |  |  | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | RW | 406004 | 6003 | I16 |  |  | analog_value | 8031 | seconds | X
DisplayStartupMode | 4 | What to display during device startup | X | 6 | 8 | Holding | RW | 406005 | 6004 | U8
display_value_time_ms | 2000 | For how long to show the value in the display before switching to the unit | I | 8 | 0 | Holding | RW | 408001 | 8000 | I16
display_unit_time_ms | 600 | For how long to show the unit in the display before switching to the value | I | 8 | 2 | Holding | RW | 408002 | 8001 | I16
display_toggle_time_ms | 5000 | For how long to show each measurement before switching to the next one | I | 8 | 4 | Holding | RW | 408003 | 8002 | I16
display_mode | 0 | Select presentation mode for the display | X | 8 | 6 | Holding | RW | 408004 | 8003 | U8
rt_exttime_mode | 0 | How to show the timer in the display | X | 8 | 7 | Holding | RW | 408005 | 8004 | U8
rt_exttime_step_size | 15 | Step size in minutes for each button press | X | 8 | 8 | Holding | RW | 408006 | 8005 | U8 |  |  | analog_value | 11000 | minutes | X
rt_exttime_steps | 6 | Number of steps before cycling back to off | X | 8 | 9 | Holding | RW | 408007 | 8006 | U8 |  |  | analog_value | 11001 |  | X
display_scroll_speed | 100 | Time in ms between scrolling one pixel | I | 8 | 10 | Holding | RW | 408008 | 8007 | I16
rt_exttime_timeleft | 0 | Time remaining | I | 8 | 12 | Holding | RW | 408009 | 8008 | I16 |  |  | analog_value | 11002 | minutes | X
display_frame_1_value | 0 | Value to show on the display in frame 1 | X | 8 | 14 | Holding | RW | 408010 | 8009 | U8
display_frame_2_value | 0 | Value to show on the display in frame 2 | X | 8 | 15 | Holding | RW | 408011 | 8010 | U8
display_frame_3_value | 0 | Value to show on the display in frame 3 | X | 8 | 16 | Holding | RW | 408012 | 8011 | U8
display_frame_4_value | 0 | Value to show on the display in frame 4 | X | 8 | 17 | Holding | RW | 408013 | 8012 | U8
display_frame_5_value | 0 | Value to show on the display in frame 5 | X | 8 | 18 | Holding | RW | 408014 | 8013 | U8
display_frame_6_value | 0 | Value to show on the display in frame 6 | X | 8 | 19 | Holding | RW | 408015 | 8014 | U8
rt_exttime_animate | 1 | Show animation in timer view | L | 8 | 20 | Coil | RW | 008001 | 8000 | U8
rt_exttime_indicate | 0 | Indicate with LED if timer is active | L | 8 | 21 | Coil | RW | 008002 | 8001 | U8
rt_exttime_state | 0 | Current timer state | L | 8 | 22 | Coil | RW | 008003 | 8002 | U8 |  |  | binary_value | 11000
out_ch_1 |  | This is the calculated value for this output | R | 8 | 23 | Input | R | 308001 308002 | 8000 8001 | REGx2I32SO | 1000 | 0 | analog_value | 11003
out_ch_1_combine | 0 | Select how to combine the source values | X | 8 | 26 | Holding | RW | 408016 | 8015 | U8
out_ch_1_enable | 1 | Enable the output mapping | L | 8 | 27 | Coil | RW | 008004 | 8003 | U8 |  |  | binary_value | 11001 |  | X
out_ch_1_source_1 | 0 | First input source for output 1 | X | 8 | 28 | Holding | RW | 408017 | 8016 | U8
out_ch_1_source_1_map_function | 0 | Select how to combine the source values | X | 8 | 29 | Holding | RW | 408018 | 8017 | U8
out_ch_1_source_1_map_max | 25 | This value on the source channel should map to 100% output | R | 8 | 30 | Holding | RW | 408019 408020 | 8018 8019 | REGx2I32SO | 1000 | 0
out_ch_1_source_1_map_min | 20 | This value on the source channel should map to 0% output | R | 8 | 33 | Holding | RW | 408021 408022 | 8020 8021 | REGx2I32SO | 1000 | 0
out_ch_1_source_2 | 0 | Second input source for output 1 | X | 8 | 36 | Holding | RW | 408023 | 8022 | U8
out_ch_1_source_2_map_function | 0 | Select how to combine the source values | X | 8 | 37 | Holding | RW | 408024 | 8023 | U8
out_ch_1_source_2_map_max | 85 | This value on the source channel should map to 100% output | R | 8 | 38 | Holding | RW | 408025 408026 | 8024 8025 | REGx2I32SO | 1000 | 0
out_ch_1_source_2_map_min | 50 | This value on the source channel should map to 0% output | R | 8 | 41 | Holding | RW | 408027 408028 | 8026 8027 | REGx2I32SO | 1000 | 0
out_ch_1_source_3 | 0 | Third input source for output 1 | X | 8 | 44 | Holding | RW | 408029 | 8028 | U8
out_ch_1_source_3_map_function | 0 | Select how to combine the source values | X | 8 | 45 | Holding | RW | 408030 | 8029 | U8
out_ch_1_source_3_map_max | 500 | This value on the source channel should map to 100% output | R | 8 | 46 | Holding | RW | 408031 408032 | 8030 8031 | REGx2I32SO | 1000 | 0
out_ch_1_source_3_map_min | 0 | This value on the source channel should map to 0% output | R | 8 | 49 | Holding | RW | 408033 408034 | 8032 8033 | REGx2I32SO | 1000 | 0
out_ch_1_source_4 | 0 | Forth input source for output 1 | X | 8 | 52 | Holding | RW | 408035 | 8034 | U8
out_ch_1_source_4_map_function | 0 | Select how to combine the source values | X | 8 | 53 | Holding | RW | 408036 | 8035 | U8
out_ch_1_source_4_map_max | 1500 | This value on the source channel should map to 100% output | R | 8 | 54 | Holding | RW | 408037 408038 | 8036 8037 | REGx2I32SO | 1000 | 0
out_ch_1_source_4_map_min | 400 | This value on the source channel should map to 0% output | R | 8 | 57 | Holding | RW | 408039 408040 | 8038 8039 | REGx2I32SO | 1000 | 0
out_ch_1_source_calc_1 |  | This is the calculated contribution from source 1 for this output | R | 8 | 60 | Input | R | 308003 308004 | 8002 8003 | REGx2I32SO | 1000 | 0
out_ch_1_source_calc_2 |  | This is the calculated contribution from source 2 for this output | R | 8 | 63 | Input | R | 308005 308006 | 8004 8005 | REGx2I32SO | 1000 | 0
out_ch_1_source_calc_3 |  | This is the calculated contribution from source 3 for this output | R | 8 | 66 | Input | R | 308007 308008 | 8006 8007 | REGx2I32SO | 1000 | 0
out_ch_1_source_calc_4 |  | This is the calculated contribution from source 4 for this output | R | 8 | 69 | Input | R | 308009 308010 | 8008 8009 | REGx2I32SO | 1000 | 0
out_ch_2 |  | This is the calculated value for this output | R | 8 | 72 | Input | R | 308011 308012 | 8010 8011 | REGx2I32SO | 1000 | 0 | analog_value | 11004
out_ch_2_combine | 0 | Select how to combine the source values | X | 8 | 75 | Holding | RW | 408041 | 8040 | U8
out_ch_2_enable | 1 | Enable the output mapping | L | 8 | 76 | Coil | RW | 008005 | 8004 | U8 |  |  | binary_value | 11002 |  | X
out_ch_2_source_1 | 0 | First input source for output 2 | X | 8 | 77 | Holding | RW | 408042 | 8041 | U8
out_ch_2_source_1_map_function | 0 | Select how to combine the source values | X | 8 | 78 | Holding | RW | 408043 | 8042 | U8
out_ch_2_source_1_map_max | 25 | This value on the source channel should map to 100% output | R | 8 | 79 | Holding | RW | 408044 408045 | 8043 8044 | REGx2I32SO | 1000 | 0
out_ch_2_source_1_map_min | 20 | This value on the source channel should map to 0% output | R | 8 | 82 | Holding | RW | 408046 408047 | 8045 8046 | REGx2I32SO | 1000 | 0
out_ch_2_source_2 | 0 | Second input source for output 2 | X | 8 | 85 | Holding | RW | 408048 | 8047 | U8
out_ch_2_source_2_map_function | 0 | Select how to combine the source values | X | 8 | 86 | Holding | RW | 408049 | 8048 | U8
out_ch_2_source_2_map_max | 85 | This value on the source channel should map to 100% output | R | 8 | 87 | Holding | RW | 408050 408051 | 8049 8050 | REGx2I32SO | 1000 | 0
out_ch_2_source_2_map_min | 50 | This value on the source channel should map to 0% output | R | 8 | 90 | Holding | RW | 408052 408053 | 8051 8052 | REGx2I32SO | 1000 | 0
out_ch_2_source_3 | 0 | Third input source for output 2 | X | 8 | 93 | Holding | RW | 408054 | 8053 | U8
out_ch_2_source_3_map_function | 0 | Select how to combine the source values | X | 8 | 94 | Holding | RW | 408055 | 8054 | U8
out_ch_2_source_3_map_max | 500 | This value on the source channel should map to 100% output | R | 8 | 95 | Holding | RW | 408056 408057 | 8055 8056 | REGx2I32SO | 1000 | 0
out_ch_2_source_3_map_min | 0 | This value on the source channel should map to 0% output | R | 8 | 98 | Holding | RW | 408058 408059 | 8057 8058 | REGx2I32SO | 1000 | 0
out_ch_2_source_4 | 0 | Forth input source for output 2 | X | 8 | 101 | Holding | RW | 408060 | 8059 | U8
out_ch_2_source_4_map_function | 0 | Select how to combine the source values | X | 8 | 102 | Holding | RW | 408061 | 8060 | U8
out_ch_2_source_4_map_max | 1500 | This value on the source channel should map to 100% output | R | 8 | 103 | Holding | RW | 408062 408063 | 8061 8062 | REGx2I32SO | 1000 | 0
out_ch_2_source_4_map_min | 400 | This value on the source channel should map to 0% output | R | 8 | 106 | Holding | RW | 408064 408065 | 8063 8064 | REGx2I32SO | 1000 | 0
out_ch_2_source_calc_1 |  | This is the calculated contribution from source 1 for this output | R | 8 | 109 | Input | R | 308013 308014 | 8012 8013 | REGx2I32SO | 1000 | 0
out_ch_2_source_calc_2 |  | This is the calculated contribution from source 2 for this output | R | 8 | 112 | Input | R | 308015 308016 | 8014 8015 | REGx2I32SO | 1000 | 0
out_ch_2_source_calc_3 |  | This is the calculated contribution from source 3 for this output | R | 8 | 115 | Input | R | 308017 308018 | 8016 8017 | REGx2I32SO | 1000 | 0
out_ch_2_source_calc_4 |  | This is the calculated contribution from source 4 for this output | R | 8 | 118 | Input | R | 308019 308020 | 8018 8019 | REGx2I32SO | 1000 | 0
out_ch_3 |  | This is the calculated value for this output | R | 8 | 121 | Input | R | 308021 308022 | 8020 8021 | REGx2I32SO | 1000 | 0 | analog_value | 11005
out_ch_3_combine | 0 | Select how to combine the source values | X | 8 | 124 | Holding | RW | 408066 | 8065 | U8
out_ch_3_enable | 1 | Enable the output mapping | L | 8 | 125 | Coil | RW | 008006 | 8005 | U8 |  |  | binary_value | 11003 |  | X
out_ch_3_source_1 | 0 | First input source for output 3 | X | 8 | 126 | Holding | RW | 408067 | 8066 | U8
out_ch_3_source_1_map_function | 0 | Select how to combine the source values | X | 8 | 127 | Holding | RW | 408068 | 8067 | U8
out_ch_3_source_1_map_max | 25 | This value on the source channel should map to 100% output | R | 8 | 128 | Holding | RW | 408069 408070 | 8068 8069 | REGx2I32SO | 1000 | 0
out_ch_3_source_1_map_min | 20 | This value on the source channel should map to 0% output | R | 8 | 131 | Holding | RW | 408071 408072 | 8070 8071 | REGx2I32SO | 1000 | 0
out_ch_3_source_2 | 0 | Second input source for output 3 | X | 8 | 134 | Holding | RW | 408073 | 8072 | U8
out_ch_3_source_2_map_function | 0 | Select how to combine the source values | X | 8 | 135 | Holding | RW | 408074 | 8073 | U8
out_ch_3_source_2_map_max | 85 | This value on the source channel should map to 100% output | R | 8 | 136 | Holding | RW | 408075 408076 | 8074 8075 | REGx2I32SO | 1000 | 0
out_ch_3_source_2_map_min | 50 | This value on the source channel should map to 0% output | R | 8 | 139 | Holding | RW | 408077 408078 | 8076 8077 | REGx2I32SO | 1000 | 0
out_ch_3_source_3 | 0 | Third input source for output 3 | X | 8 | 142 | Holding | RW | 408079 | 8078 | U8
out_ch_3_source_3_map_function | 0 | Select how to combine the source values | X | 8 | 143 | Holding | RW | 408080 | 8079 | U8
out_ch_3_source_3_map_max | 500 | This value on the source channel should map to 100% output | R | 8 | 144 | Holding | RW | 408081 408082 | 8080 8081 | REGx2I32SO | 1000 | 0
out_ch_3_source_3_map_min | 0 | This value on the source channel should map to 0% output | R | 8 | 147 | Holding | RW | 408083 408084 | 8082 8083 | REGx2I32SO | 1000 | 0
out_ch_3_source_4 | 0 | Forth input source for output 3 | X | 8 | 150 | Holding | RW | 408085 | 8084 | U8
out_ch_3_source_4_map_function | 0 | Select how to combine the source values | X | 8 | 151 | Holding | RW | 408086 | 8085 | U8
out_ch_3_source_4_map_max | 1500 | This value on the source channel should map to 100% output | R | 8 | 152 | Holding | RW | 408087 408088 | 8086 8087 | REGx2I32SO | 1000 | 0
out_ch_3_source_4_map_min | 400 | This value on the source channel should map to 0% output | R | 8 | 155 | Holding | RW | 408089 408090 | 8088 8089 | REGx2I32SO | 1000 | 0
out_ch_3_source_calc_1 |  | This is the calculated contribution from source 1 for this output | R | 8 | 158 | Input | R | 308023 308024 | 8022 8023 | REGx2I32SO | 1000 | 0
out_ch_3_source_calc_2 |  | This is the calculated contribution from source 2 for this output | R | 8 | 161 | Input | R | 308025 308026 | 8024 8025 | REGx2I32SO | 1000 | 0
out_ch_3_source_calc_3 |  | This is the calculated contribution from source 3 for this output | R | 8 | 164 | Input | R | 308027 308028 | 8026 8027 | REGx2I32SO | 1000 | 0
out_ch_3_source_calc_4 |  | This is the calculated contribution from source 4 for this output | R | 8 | 167 | Input | R | 308029 308030 | 8028 8029 | REGx2I32SO | 1000 | 0
out_ch_4 |  | This is the calculated value for this output | R | 8 | 170 | Input | R | 308031 308032 | 8030 8031 | REGx2I32SO | 1000 | 0 | analog_value | 11006
out_ch_4_combine | 0 | Select how to combine the source values | X | 8 | 173 | Holding | RW | 408091 | 8090 | U8
out_ch_4_enable | 1 | Enable the output mapping | L | 8 | 174 | Coil | RW | 008007 | 8006 | U8 |  |  | binary_value | 11004 |  | X
out_ch_4_source_1 | 0 | First input source for output 4 | X | 8 | 175 | Holding | RW | 408092 | 8091 | U8
out_ch_4_source_1_map_function | 0 | Select how to combine the source values | X | 8 | 176 | Holding | RW | 408093 | 8092 | U8
out_ch_4_source_1_map_max | 25 | This value on the source channel should map to 100% output | R | 8 | 177 | Holding | RW | 408094 408095 | 8093 8094 | REGx2I32SO | 1000 | 0
out_ch_4_source_1_map_min | 20 | This value on the source channel should map to 0% output | R | 8 | 180 | Holding | RW | 408096 408097 | 8095 8096 | REGx2I32SO | 1000 | 0
out_ch_4_source_2 | 0 | Second input source for output 4 | X | 8 | 183 | Holding | RW | 408098 | 8097 | U8
out_ch_4_source_2_map_function | 0 | Select how to combine the source values | X | 8 | 184 | Holding | RW | 408099 | 8098 | U8
out_ch_4_source_2_map_max | 85 | This value on the source channel should map to 100% output | R | 8 | 185 | Holding | RW | 408100 408101 | 8099 8100 | REGx2I32SO | 1000 | 0
out_ch_4_source_2_map_min | 50 | This value on the source channel should map to 0% output | R | 8 | 188 | Holding | RW | 408102 408103 | 8101 8102 | REGx2I32SO | 1000 | 0
out_ch_4_source_3 | 0 | Third input source for output 4 | X | 8 | 191 | Holding | RW | 408104 | 8103 | U8
out_ch_4_source_3_map_function | 0 | Select how to combine the source values | X | 8 | 192 | Holding | RW | 408105 | 8104 | U8
out_ch_4_source_3_map_max | 500 | This value on the source channel should map to 100% output | R | 8 | 193 | Holding | RW | 408106 408107 | 8105 8106 | REGx2I32SO | 1000 | 0
out_ch_4_source_3_map_min | 0 | This value on the source channel should map to 0% output | R | 8 | 196 | Holding | RW | 408108 408109 | 8107 8108 | REGx2I32SO | 1000 | 0
out_ch_4_source_4 | 0 | Forth input source for output 4 | X | 8 | 199 | Holding | RW | 408110 | 8109 | U8
out_ch_4_source_4_map_function | 0 | Select how to combine the source values | X | 8 | 200 | Holding | RW | 408111 | 8110 | U8
out_ch_4_source_4_map_max | 1500 | This value on the source channel should map to 100% output | R | 8 | 201 | Holding | RW | 408112 408113 | 8111 8112 | REGx2I32SO | 1000 | 0
out_ch_4_source_4_map_min | 400 | This value on the source channel should map to 0% output | R | 8 | 204 | Holding | RW | 408114 408115 | 8113 8114 | REGx2I32SO | 1000 | 0
out_ch_4_source_calc_1 |  | This is the calculated contribution from source 1 for this output | R | 8 | 207 | Input | R | 308033 308034 | 8032 8033 | REGx2I32SO | 1000 | 0
out_ch_4_source_calc_2 |  | This is the calculated contribution from source 2 for this output | R | 8 | 210 | Input | R | 308035 308036 | 8034 8035 | REGx2I32SO | 1000 | 0
out_ch_4_source_calc_3 |  | This is the calculated contribution from source 3 for this output | R | 8 | 213 | Input | R | 308037 308038 | 8036 8037 | REGx2I32SO | 1000 | 0
out_ch_4_source_calc_4 |  | This is the calculated contribution from source 4 for this output | R | 8 | 216 | Input | R | 308039 308040 | 8038 8039 | REGx2I32SO | 1000 | 0
out_relay |  | This is the calculated value for the relay control function | R | 8 | 219 | Input | R | 308041 308042 | 8040 8041 | REGx2I32SO | 1000 | 0
out_relay_combine | 0 | Select how to combine the source values | X | 8 | 222 | Holding | RW | 408116 | 8115 | U8
out_relay_enable | 1 | Enable the relay function mapping | L | 8 | 223 | Coil | RW | 008008 | 8007 | U8
out_relay_indicate | 0 | Indicate with LED if relay is active | L | 8 | 224 | Coil | RW | 008009 | 8008 | U8
out_relay_limit_OFF | 0 | This is the limit (0 to 1) where to deactivate the relay | R | 8 | 225 | Holding | RW | 408117 408118 | 8116 8117 | REGx2I32SO | 1000 | 0
out_relay_limit_ON | 100 | This is the limit (0 to 100%) where to activate the relay | R | 8 | 228 | Holding | RW | 408119 408120 | 8118 8119 | REGx2I32SO | 1000 | 0
out_relay_source_1 | 4 | First input source for the relay control function | X | 8 | 231 | Holding | RW | 408121 | 8120 | U8
out_relay_source_1_map_function | 0 | Select how to combine the source values | X | 8 | 232 | Holding | RW | 408122 | 8121 | U8
out_relay_source_1_map_max | 1000 | This value on the source channel should map to 1 | R | 8 | 233 | Holding | RW | 408123 408124 | 8122 8123 | REGx2I32SO | 1000 | 0
out_relay_source_1_map_min | 500 | This value on the source channel should map to 0 | R | 8 | 236 | Holding | RW | 408125 408126 | 8124 8125 | REGx2I32SO | 1000 | 0
out_relay_source_2 | 0 | Second input source for the relay control function | X | 8 | 239 | Holding | RW | 408127 | 8126 | U8
out_relay_source_2_map_function | 0 | Select how to combine the source values | X | 8 | 240 | Holding | RW | 408128 | 8127 | U8
out_relay_source_2_map_max | 24 | This value on the source channel should map to 1 | R | 8 | 241 | Holding | RW | 408129 408130 | 8128 8129 | REGx2I32SO | 1000 | 0
out_relay_source_2_map_min | 22 | This value on the source channel should map to 0 | R | 8 | 244 | Holding | RW | 408131 408132 | 8130 8131 | REGx2I32SO | 1000 | 0
out_relay_source_3 | 0 | Third input source for the relay control function | X | 8 | 247 | Holding | RW | 408133 | 8132 | U8
out_relay_source_3_map_function | 0 | Select how to combine the source values | X | 8 | 248 | Holding | RW | 408134 | 8133 | U8
out_relay_source_3_map_max | 25 | This value on the source channel should map to 1 | R | 8 | 249 | Holding | RW | 408135 408136 | 8134 8135 | REGx2I32SO | 1000 | 0
out_relay_source_3_map_min | 15 | This value on the source channel should map to 0 | R | 8 | 252 | Holding | RW | 408137 408138 | 8136 8137 | REGx2I32SO | 1000 | 0
out_relay_source_4 | 0 | Forth input source for the relay control function | X | 8 | 255 | Holding | RW | 408139 | 8138 | U8
out_relay_source_4_map_function | 0 | Select how to combine the source values | X | 8 | 256 | Holding | RW | 408140 | 8139 | U8
out_relay_source_4_map_max | 25 | This value on the source channel should map to 1 | R | 8 | 257 | Holding | RW | 408141 408142 | 8140 8141 | REGx2I32SO | 1000 | 0
out_relay_source_4_map_min | 15 | This value on the source channel should map to 0 | R | 8 | 260 | Holding | RW | 408143 408144 | 8142 8143 | REGx2I32SO | 1000 | 0
out_relay_source_calc_1 |  | This is the calculated contribution from source 1 for the relay control function | R | 8 | 263 | Input | R | 308043 308044 | 8042 8043 | REGx2I32SO | 1000 | 0
out_relay_source_calc_2 |  | This is the calculated contribution from source 2 for the relay control function | R | 8 | 266 | Input | R | 308045 308046 | 8044 8045 | REGx2I32SO | 1000 | 0
out_relay_source_calc_3 |  | This is the calculated contribution from source 3 for the relay control function | R | 8 | 269 | Input | R | 308047 308048 | 8046 8047 | REGx2I32SO | 1000 | 0
out_relay_source_calc_4 |  | This is the calculated contribution from source 4 for the relay control function | R | 8 | 272 | Input | R | 308049 308050 | 8048 8049 | REGx2I32SO | 1000 | 0
rt_text_display_scroll_mode | 0 | Scroll mode | X | 8 | 277 | Holding | RW | 408147 | 8146 | U8 |  |  | multi_state_value | 11002 |  | X
rt_text_display_scroll_speed | 100 | Time in ms between scrolling one pixel | I | 8 | 278 | Holding | RW | 408148 | 8147 | I16 |  |  | analog_value | 11007 | milliseconds | X
rt_text_visability | 0 | When to show the custom text | X | 8 | 280 | Holding | RW | 408149 | 8148 | U8 |  |  | multi_state_value | 11003 |  | X
rt_text_timeleft | 0 | Time to show the custom text | I | 8 | 281 | Holding | RW | 408150 | 8149 | I16 |  |  | analog_value | 11008 | seconds | X
rt_text_row_1 |  | String to show on row 1 in the display | $ | 8 | 283 | Holding | RW | 408151 - 408182 | 8150 - 8181 | STRING |  |  | characterstring_value | 11000 |  | X
rt_text_row_2 |  | String to show on row 2 in the display | $ | 8 | 286 | Holding | RW | 408183 - 408214 | 8182 - 8213 | STRING |  |  | characterstring_value | 11001 |  | X
SCD40_ASC_enable | 1 | Enable automatic calibration of CO2 sensor | L | 10 | 50 | Coil | RW | 000101 | 100 | LOGIC
SCD40_ASC_target | 400 | Automatic calibration of CO2 sensor target | I | 10 | 51 | Holding | RW | 400101 | 100 | I16
SCD40_factory_reset | 1 | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset | L | 10 | 53 | Coil | RW | 000102 | 101 | LOGIC
SCD40_FRC_result | 0 | Calculated offset after calibration or -9999 if failed. | I | 10 | 54 | Holding | RW | 400102 | 101 | I16
SCD40_FRC_enable | 0 | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done | L | 10 | 56 | Coil | RW | 000103 | 102 | LOGIC
SCD40_FRC_target | 400 | Current actual CO2 value to calibrate to | I | 10 | 57 | Holding | RW | 400103 | 102 | I16
PLA | 254 |  | X | 241 | 0
ELA | 30 |  | X | 241 | 1
Ver_Minor |  |  | X | 241 | 16 | Input | R | 300007 | 6 | U8
Ver_Major |  |  | X | 241 | 17 | Input | R | 300006 | 5 | U8
MODEL_ALIAS |  | Model number | I | 241 | 36 | Input | R | 300050 | 49 | I16
Model |  | Model number | I | 241 | 36 | Input | R | 300002 | 1 | I16
Ver_Branch |  |  | X | 241 | 40 | Input | R | 300008 | 7 | U8
Ver_Number |  |  | X | 241 | 41 | Input | R | 300009 | 8 | U8
SerialNumberString | 0 |  | $ | 241 | 60
ControllerName | RegioX |  | $ | 241 | 63 | Holding | RW | 400039 - 400070 | 38 - 69 | STRING
ControllerProject | 0 |  | $ | 241 | 66
ControllerDescription |  | Controller description | $ | 241 | 69
ControllerLocation |  | Controller location | $ | 241 | 72
UptimeMillisec | 0 |  | I | 241 | 75
UptimeSec | 0 |  | H | 241 | 77
GitCommit |  | Internal revision number | I | 241 | 80 | Input | R | 300011 | 10 | I16
ModelName | 0 |  | $ | 241 | 100
VendorName | AB Regin |  | $ | 241 | 109
OSid |  | Application OPERATING_SYSTEM_ID | H | 241 | 138
BACnetCommitSettings | 0 | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | RegioX | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | BACnet APDU segment timeout | I | 242 | 69
BACnetConfLn | 125 | BACnet configuration load number | X | 242 | 71
BACnetDataLn | 124 | BACnet data load number | X | 242 | 72
BACnetWideCharacterSetEncoding | 0 | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetIpEnable | 0 | BACnet IP enable | L | 242 | 112
BACnetMaxServerCOV | 100 | BACnet max server COV | I | 242 | 135
BACnetPassword | gioP5TJBP8FASqREs6zX | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | Active Modbus unit ID | X | 242 | 172 | Holding | RW | 400002 | 1 | U8
ModbusCharTimeout_Port_1 | 3 |  | I | 242 | 197 | Holding | RW | 400008 | 7 | I16
ModbusAnswerDelay_Port_1 | 5 |  | I | 242 | 199 | Holding | RW | 400009 | 8 | I16
Mode_Port_1 | 2 | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 |  | X | 248 | 38
Baud_Port_1 | 0 | Active RS485 port baud rate | X | 248 | 41
Note on K3: LOGIC: Used for True/False values, only allowed for "Discrete inputs" and "Coils" U8: One 8 bit unsigned integer variable to/from LSB of one register I16: One 16 bit integer variable to/from one register I16SO: Floating point variable converted to 16 bit integer to/from one register. Scale and Offset used REGx2IEEE: First register: MSW of floating point variable to/from one 16-bit register (IEEE) Second register: LSW of floating point variable to/from one 16-bit register (IEEE) REGx2I32: First register: MSW of 32 bit integer variable to/from one 16-bit register Second register: LSW of 32 bit integer variable to/from one 16-bit register REGx2I32SO: First register: MSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O Second register: LSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O
Note on C5: 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on C8: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on N8: 1 = Inactive 3 = EXOline slave 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on C9: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on N9: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on C10: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on N10: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on C16: 0 = Disabled 1 = Set outputs to default values 2 = Set controller state to a default value 3 = Set outputs to default values, start device in offline mode
Note on N16: 1 = Disabled 2 = Set outputs to default values 3 = Set controller state to a default value 4 = Set outputs to default values, start device in offline mode
Note on C20: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C22: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C24: 0 = No faults 1 = Internal Error 2 = Calibration Lost during startup 4 = Calibration memory failed
Note on C33: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on C50: 0 = Off 1 = Green 2 = Yellow 3 = Red
Note on N50: 1 = Off 2 = Green 3 = Yellow 4 = Red
Note on C71: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C72: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C90: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C91: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C109: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C110: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C127: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C128: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C144: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C145: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C161: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C162: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C178: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C179: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C195: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C196: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C213: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C214: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C229: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C230: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C245: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C246: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C262: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C272: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C282: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C292: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C300: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C301: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C315: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C316: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C330: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C331: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C345: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C346: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C363: 0 = Do not display any boot screen 1 = Display device type 2 = Display device type and model 3 = Display device type, model and version 4 = Display device type, model, version and addresses
Note on C367: 0 = Alternate between available measurements and alternate between value and unit 1 = Alternate between available measurements and scroll value and unit with wraping 2 = Alternate between available measurements and scroll value and unit bounce at end of unit 3 = Scroll all measurements including units and wrap 4 = Scroll all measurements including units and bounce and the end
Note on C368: 0 = When the Timer is active always show only that value 1 = Only show value when changing and use the normal display selection to show the value
Note on C373: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C374: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C375: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C376: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C377: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C378: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C383: 0 = Use the maximum of the source values 1 = Use the minimum of the source values 2 = Use the average of the source values
Note on C385: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C386: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C389: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C390: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C393: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C394: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C397: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C398: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C406: 0 = Use the maximum of the source values 1 = Use the minimum of the source values 2 = Use the average of the source values
Note on C408: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C409: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C412: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C413: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C416: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C417: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C420: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C421: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C429: 0 = Use the maximum of the source values 1 = Use the minimum of the source values 2 = Use the average of the source values
Note on C431: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C432: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C435: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C436: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C439: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C440: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C443: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C444: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C452: 0 = Use the maximum of the source values 1 = Use the minimum of the source values 2 = Use the average of the source values
Note on C454: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C455: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C458: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C459: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C462: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C463: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C466: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C467: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C475: 0 = Use the maximum of the source values 1 = Use the minimum of the source values 2 = Use the average of the source values
Note on C480: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C481: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C484: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C485: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C488: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C489: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C492: 0 = Do not show value 1 = Temperature in degrees Celcius 2 = Temperature in degrees Fahrenheit 3 = Relative humidity in percent 4 = CO2 in PPM 5 = VOC in a value between 0 and 500 6 = Count down timer 7 = Show custom text string 1 8 = Show custom text string 2 9 = Value on universal input 1 10 = Value on universal input 2 11 = Count down timer, if active
Note on C493: 0 = Linear translation from MIN to MAX 1 = Use some log function... 2 = Use some square function...
Note on C500: 0 = Wrap text at the end 1 = Bounce between start and end position 2 = Wrap text at the end, sync row 1 and 2 3 = Bounce between start and end position, sync row 1 and 2
Note on N500: 1 = Wrap text at the end 2 = Bounce between start and end position 3 = Wrap text at the end, sync row 1 and 2 4 = Bounce between start and end position, sync row 1 and 2
Note on C502: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on N502: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on C554: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on C555: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on C557: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s