## Variables
RUX - 2.0-1-03 Variable list | [16 empty] | Revision: | A
|  |  | EXOline |  |  | Modbus | [6 empty] | BACnet
Name | Default | Description | Type | Load | Cell | Reg. Type | RW | Register | Addr | Data Type | Scale | Offset | Default BACnet name | Object type | Instance | Unit | Writeable | Variable type
ModbusListVersion |  | Modbus list version | X | 1 | 0 | Input | R | 300001 | 0 | U8
product_reset | 0 | Write to this register will trigger resets with different reset reasons | I | 1 | 1
rc_wink | 0 | Wink for this amount of time in seconds | X | 1 | 3 | Holding | RW | 400003 | 2 | U8 |  |  | Wink | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 | Commit communication settings | L | 1 | 5 | Coil | RW | 000001 | 0 | LOGIC |  |  | CommCommit | binary_value | 9001 |  | X
RC_Port1Mode | 2 | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | RW | 400005 | 4 | U8 |  |  | Port1Mode | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | RW | 400007 | 6 | U8 |  |  | Port1Baud | multi_state_value | 9101 |  | X
RC_Port1Format | 112 | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | RW | 400006 | 5 | U8 |  |  | Port1Format | multi_state_value | 9201 |  | X
SerialHigh |  | Serial number, high part | I | 1 | 15 | Input | R | 300005 | 4 | I16
SerialMid |  | Serial number, mid part | I | 1 | 17 | Input | R | 300004 | 3 | I16
SerialLow |  | Serial number, low part | I | 1 | 19 | Input | R | 300003 | 2 | I16
RC_Offline |  | Heartbeat function indicates if the device is offline or not | L | 1 | 21 | Discrete | R | 100001 | 0 | LOGIC
RC_OfflineTrigger | 0 | Write 1 to this register periodically for keep system running in normal mode, will be set to 0 by application | L | 1 | 22 | Coil | RW | 000002 | 1 | LOGIC |  |  | HeartbeatTrigger | binary_value | 9101 |  | X
RC_OfflineFunction | 0 | Offline function | X | 1 | 23 | Holding | RW | 400020 | 19 | U8 |  |  | RC_OfflineFunction | multi_state_value | 9301 |  | X
RC_OfflineCounter |  | Offline timeout counter seconds. Used to check current state of the counter, it counts from 0 at trigger up to next trigger or HEARTBEAT_OFFLINE_TIMEOUT. | I | 1 | 24 | Input | R | 300010 | 9 | I16
RC_OfflineTimeout | 10 | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. | I | 1 | 26 | Holding | RW | 400021 | 20 | I16
RgbEnable | 0 | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | RW | 000003 | 2 | LOGIC
RgbOffColor | 0 | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | RW | 400027 | 26 | U8
RgbOffTime | 500 | Off time in ms | I | 1 | 37 | Holding | RW | 400028 | 27 | I16
RgbOnColor | 252 | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | RW | 400029 | 28 | U8
RgbOnTime | 100 | On time in ms | I | 1 | 40 | Holding | RW | 400030 | 29 | I16
product_status | 0 | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | RW | 400004 | 3 | I16
RafosVerMajor |  | Platform software version, major part | X | 1 | 64 | Input | R | 300013 | 12 | U8
RafosVerMinor |  | Platform software version, minor part | X | 1 | 65 | Input | R | 300014 | 13 | U8
RafosVerBranch |  | Platform software version, branch part | X | 1 | 66 | Input | R | 300015 | 14 | U8
RafosVerNumber |  | Platform software version, number part | X | 1 | 67 | Input | R | 300016 | 15 | U8
OspreyGitCommit |  | Osprey Git commit | I | 1 | 68 | Input | R | 300017 | 16 | I16
OsId |  | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | R | 300021 | 20 | I16
VersionNumberString |  | The application version as a string | $ | 1 | 76
gitCommitHashString |  | The Full Git hash of the application | $ | 1 | 79
BleButtonMode | 3 | Function for BLE button | X | 1 | 83 | Holding | RW | 400071 | 70 | U8
BleButtonTimeout | 120 | Timeout when BLE is started with the button | I | 1 | 84 | Holding | RW | 400072 | 71 | I16
BleVerMajor |  | BLE stack version, major part | X | 1 | 98 | Input | R | 300022 | 21 | U8
BleVerMinor |  | BLE stack version, minor part | X | 1 | 99 | Input | R | 300023 | 22 | U8
BleVerBranch |  | BLE stack version, branch part | X | 1 | 100 | Input | R | 300024 | 23 | U8
BleVerNumber |  | BLE stack version, number part | X | 1 | 101 | Input | R | 300025 | 24 | U8
FusVerMajor |  | FUS stack version, major part | X | 1 | 102 | Input | R | 300026 | 25 | U8
FusVerMinor |  | FUS version, minor part | X | 1 | 103 | Input | R | 300027 | 26 | U8
FusVerBranch |  | FUS version, branch part | X | 1 | 104 | Input | R | 300028 | 27 | U8
FusVerNumber |  | FUS version, number part | X | 1 | 105 | Input | R | 300029 | 28 | U8
RC_RoomActiveSetpoint |  | Active room control setpoint | R | 2 | 31 | Input | R | 305009 | 5008 | I16SO | 10 | 0 | RC_RoomActiveSetpoint | analog_value | 10081 | degrees_celsius
RC_FanSpeed |  | Current 3-speed fan speed | X | 2 | 73 | Input | R | 305030 | 5029 | U8
RC_DisplayViewValue |  | Value to be shown in the display | R | 2 | 90 | Input | R | 305034 | 5033 | I16SO | 10 | 0 | RC_DisplayViewValue | analog_value | 10291
RC_DisplaySetpointValue |  | Setpoint display at setpoint adjustment | R | 2 | 93 | Input | R | 305035 | 5034 | I16SO | 10 | 0 | RC_DisplaySetpointValue | analog_value | 10301
RC_CO2Indicator |  | RGB CO2 indication | X | 2 | 96 | Input | R | 305036 | 5035 | U8 |  |  | RC_CO2Indicator | multi_state_value | 10021
RC_RoomSetpointHeatOff | 8 | Heating setpoint in Off state (frost protection). | R | 3 | 184 | Holding | RW | 405149 | 5148 | I16SO | 10 | 0 | RC_RoomSetpointHeatOff | analog_value | 10331 | degrees_celsius | X
RC_RoomSetpointHeatUnoccupied | 15 | Heating setpoint in Unoccupied state. | R | 3 | 187 | Holding | RW | 405150 | 5149 | I16SO | 10 | 0 | RC_RoomSetpointHeatUnoccupied | analog_value | 10341 | degrees_celsius | X
RC_RoomSetpointHeatStandby | 19 | Heating setpoint in Standby state. | R | 3 | 190 | Holding | RW | 405151 | 5150 | I16SO | 10 | 0 | RC_RoomSetpointHeatStandby | analog_value | 10351 | degrees_celsius | X
RC_RoomSetpointHeatOccupied | 22 | Heating setpoint in Occupied state. | R | 3 | 193 | Holding | RW | 405152 | 5151 | I16SO | 10 | 0 | RC_RoomSetpointHeatOccupied | analog_value | 10361 | degrees_celsius | X
RC_RoomSetpointCoolUnoccupied | 30 | Cooling setpoint in Unoccupied state. | R | 3 | 196 | Holding | RW | 405153 | 5152 | I16SO | 10 | 0 | RC_RoomSetpointCoolUnoccupied | analog_value | 10371 | degrees_celsius | X
RC_RoomSetpointCoolStandby | 27 | Cooling setpoint in Standby state. | R | 3 | 199 | Holding | RW | 405154 | 5153 | I16SO | 10 | 0 | RC_RoomSetpointCoolStandby | analog_value | 10381 | degrees_celsius | X
RC_RoomSetpointCoolOccupied | 24 | Cooling setpoint in Occupied state. | R | 3 | 202 | Holding | RW | 405155 | 5154 | I16SO | 10 | 0 | RC_RoomSetpointCoolOccupied | analog_value | 10391 | degrees_celsius | X
RC_RoomSetpointOffset | 0 | Setpoint offset. Effective in Standby state or higher. | R | 3 | 205 | Holding | RW | 405156 | 5155 | I16SO | 10 | 0 | RC_RoomSetpointOffset | analog_value | 10401 | degrees_celsius | X
RC_RoomSetpointOffsetMaxPos | 3 | Maximum positive setpoint offset. | R | 3 | 208 | Holding | RW | 405157 | 5156 | I16SO | 10 | 0 | RC_RoomSetpointOffsetMaxPos | analog_value | 10411 | degrees_celsius | X
RC_RoomSetpointOffsetMaxNeg | 3 | Maximum negative setpoint offset. | R | 3 | 211 | Holding | RW | 405158 | 5157 | I16SO | 10 | 0 | RC_RoomSetpointOffsetMaxNeg | analog_value | 10421 | degrees_celsius | X
RC_FanSelect | 4 | Fan speed setting | X | 3 | 281 | Holding | RW | 405185 | 5184 | U8 |  |  | RC_FanSelect | multi_state_value | 10031
RC_RoomTempRemote | 22 | Remote setting of room temperature | R | 3 | 318 | Holding | RW | 405210 | 5209 | I16SO | 10 | 0 | RC_RoomTempRemote | analog_value | 10611 | degrees_celsius | X
RC_CO2LevelRemote | 400 | Remote setting of room CO2 level | R | 3 | 321 | Holding | RW | 405211 | 5210 | I16SO | 10 | 0 | RC_CO2LevelRemote | analog_value | 10621 | parts_per_million | X
RC_HumidityRemote | 50 | Remote setting of relative humidity | R | 3 | 339 | Holding | RW | 405217 | 5216 | I16SO | 10 | 0 | RC_HumidityRemote | analog_value | 10681 | percent_relative_humidity | X
RC_VOCRemote | 100 | Remote setting of VOC index | R | 3 | 342 | Holding | RW | 405218 | 5217 | I16SO | 10 | 0 | RC_VOCRemote | analog_value | 10691 |  | X
RC_RoomTempRemoteSelect | 0 | Enable remote setting of room temperature | L | 3 | 345 | Coil | RW | 005022 | 5021 | LOGIC |  |  | RC_RoomTempRemoteSelect | binary_value | 10321 |  | X
RC_CO2LevelRemoteSelect | 0 | Enable remote setting of room CO2 level | L | 3 | 346 | Coil | RW | 005023 | 5022 | LOGIC |  |  | RC_CO2LevelRemoteSelect | binary_value | 10331 |  | X
RC_HumidityRemoteSelect | 0 | Enable remote setting of relative humidity | L | 3 | 352 | Coil | RW | 005029 | 5028 | LOGIC |  |  | RC_HumidityRemoteSelect | binary_value | 10391 |  | X
RC_VOCRemoteSelect | 0 | Enable remote setting of VOC index | L | 3 | 353 | Coil | RW | 005030 | 5029 | LOGIC |  |  | RC_VOCRemoteSelect | binary_value | 10401 |  | X
RC_DisplayViewMode | 0 | Select value to be shown in the display | X | 3 | 442 | Holding | RW | 405271 | 5270 | U8 |  |  | RC_DisplayViewMode | multi_state_value | 10221 |  | X
RC_DisplaySetpointMode | 0 | Select setpoint display at setpoint adjustment | X | 3 | 443 | Holding | RW | 405272 | 5271 | U8 |  |  | RC_DisplaySetpointMode | multi_state_value | 10231 |  | X
RC_CO2FilterTime | 5 | CO2 filter time (0 to 17200 seconds) | I | 3 | 492 | Holding | RW | 405301 | 5300 | I16
RC_RHFilterTime | 5 | RH filter time (0 to 17200 seconds) | I | 3 | 494 | Holding | RW | 405302 | 5301 | I16
RC_TempFilterTime | 5 | Temperature filter time (0 to 17200 seconds) | I | 3 | 496 | Holding | RW | 405303 | 5302 | I16
RC_VOCFilterTime | 5 | VOC index filter time (0 to 17200 seconds) | I | 3 | 500 | Holding | RW | 405305 | 5304 | I16
RC_CO2LevelYellow | 800 | CO2 level for yellow led | R | 3 | 502 | Holding | RW | 405306 | 5305 | I16SO | 1 | 0 | RC_CO2LevelYellow | analog_value | 10891 | parts_per_million | X
RC_CO2LevelRed | 1000 | CO2 level for red led | R | 3 | 505 | Holding | RW | 405307 | 5306 | I16SO | 1 | 0 | RC_CO2LevelRed | analog_value | 10901 | parts_per_million | X
RC_CO2SetIndication | 0 | Enable/disable CO2 led indication | X | 3 | 508 | Holding | RW | 405308 | 5307 | U8
RC_TemperatureCO2 | 0 | Alternate temperature/CO2 display | L | 3 | 517 | Coil | RW | 005045 | 5044 | LOGIC
RC_RuxControllerMode | 0 | Current controller mode for RUX devices | X | 3 | 550 | Holding | RW | 405325 | 5324 | U8
IoAnaIn_5_value |  | Filtered value from sensor | R | 4 | 200 | Input | R | 301101 301102 | 1100 1101 | REGx2I32SO | 100 | 0 | IoAnaIn_5_value | analog_value | 1005
IoAnaIn_6_value |  | Filtered value from sensor | R | 4 | 250 | Input | R | 301126 301127 | 1125 1126 | REGx2I32SO | 100 | 0 | IoAnaIn_6_value | analog_value | 1006
IoAnaIn_7_value |  | Filtered value from sensor | R | 4 | 300 | Input | R | 301151 301152 | 1150 1151 | REGx2I32SO | 100 | 0 | IoAnaIn_7_value | analog_value | 1007
IoAnaIn_8_value |  | Filtered value from sensor | R | 4 | 350 | Input | R | 301176 301177 | 1175 1176 | REGx2I32SO | 100 | 0 | IoAnaIn_8_value | analog_value | 1008
Disp_BrightnessFull | 100 | Display brightness, full (%) | X | 6 | 0 | Holding | RW | 406001 | 6000 | U8 |  |  | Disp_BrightnessFull | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | Display brightness, dimmed (%) | X | 6 | 1 | Holding | RW | 406002 | 6001 | U8 |  |  | Disp_BrightnessDim | analog_value | 8011 | percent | X
Disp_TimeFull | 30 | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | RW | 406003 | 6002 | I16 |  |  | Disp_TimeFull | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | RW | 406004 | 6003 | I16 |  |  | Disp_TimeDim | analog_value | 8031 | seconds | X
DisplayStartupMode | 4 | What to display during device startup | X | 6 | 8 | Holding | RW | 406005 | 6004 | U8
rt_text_font | 0 | What font to use for the display text | X | 8 | 275 | Holding | RW | 408145 | 8144 | U8 |  |  | rt_text_font | multi_state_value | 11000 |  | X
rt_text_mode | 0 | Single or dual row text in display | X | 8 | 276 | Holding | RW | 408146 | 8145 | U8 |  |  | rt_text_mode | multi_state_value | 11001 |  | X
rt_text_display_scroll_mode | 0 | Scroll mode | X | 8 | 277 | Holding | RW | 408147 | 8146 | U8 |  |  | rt_text_display_scroll_mode | multi_state_value | 11002 |  | X
rt_text_display_scroll_speed | 100 | Time in ms between scrolling one pixel | I | 8 | 278 | Holding | RW | 408148 | 8147 | I16 |  |  | rt_text_display_scroll_speed | analog_value | 11007 | milliseconds | X
rt_text_visability | 0 | When to show the custom text | X | 8 | 280 | Holding | RW | 408149 | 8148 | U8 |  |  | rt_text_visability | multi_state_value | 11003 |  | X
rt_text_timeleft | 0 | Time to show the custom text | I | 8 | 281 | Holding | RW | 408150 | 8149 | I16 |  |  | rt_text_timeleft | analog_value | 11008 | seconds | X
rt_text_row_1 |  | String to show on row 1 in the display | $ | 8 | 283 | Holding | RW | 408151 - 408182 | 8150 - 8181 | STRING |  |  | rt_text_row_1 | characterstring_value | 11000 |  | X
rt_text_row_2 |  | String to show on row 2 in the display | $ | 8 | 286 | Holding | RW | 408183 - 408214 | 8182 - 8213 | STRING |  |  | rt_text_row_2 | characterstring_value | 11001 |  | X
rt_fb_visability | 0 | When to show the custom frame buffer | X | 8 | 289 | Holding | RW | 408215 | 8214 | U8 |  |  | rt_fb_visability | multi_state_value | 11004 |  | X
rt_fb_timeleft | 0 | Time to show the custom frame buffer | I | 8 | 290 | Holding | RW | 408216 | 8215 | I16 |  |  | rt_fb_timeleft | analog_value | 11009 | seconds | X
rt_fb_row0 | 0 | Frame buffer data for row 0 on the display | H | 8 | 292 | Holding | RW | 408217 408218 | 8216 8217 | REGx2I32 |  |  | rt_fb_row0 | analog_value | 11010 | seconds | X
rt_fb_row1 | 0 | Frame buffer data for row 1 on the display | H | 8 | 295 | Holding | RW | 408219 408220 | 8218 8219 | REGx2I32 |  |  | rt_fb_row1 | analog_value | 11011 | seconds | X
rt_fb_row2 | 0 | Frame buffer data for row 2 on the display | H | 8 | 298 | Holding | RW | 408221 408222 | 8220 8221 | REGx2I32 |  |  | rt_fb_row2 | analog_value | 11012 | seconds | X
rt_fb_row3 | 0 | Frame buffer data for row 3 on the display | H | 8 | 301 | Holding | RW | 408223 408224 | 8222 8223 | REGx2I32 |  |  | rt_fb_row3 | analog_value | 11013 | seconds | X
rt_fb_row4 | 0 | Frame buffer data for row 4 on the display | H | 8 | 304 | Holding | RW | 408225 408226 | 8224 8225 | REGx2I32 |  |  | rt_fb_row4 | analog_value | 11014 | seconds | X
rt_fb_row5 | 0 | Frame buffer data for row 5 on the display | H | 8 | 307 | Holding | RW | 408227 408228 | 8226 8227 | REGx2I32 |  |  | rt_fb_row5 | analog_value | 11015 | seconds | X
rt_fb_row6 | 0 | Frame buffer data for row 6 on the display | H | 8 | 310 | Holding | RW | 408229 408230 | 8228 8229 | REGx2I32 |  |  | rt_fb_row6 | analog_value | 11016 | seconds | X
rt_fb_row7 | 0 | Frame buffer data for row 7 on the display | H | 8 | 313 | Holding | RW | 408231 408232 | 8230 8231 | REGx2I32 |  |  | rt_fb_row7 | analog_value | 11017 | seconds | X
rt_fb_row8 | 0 | Frame buffer data for row 8 on the display | H | 8 | 316 | Holding | RW | 408233 408234 | 8232 8233 | REGx2I32 |  |  | rt_fb_row8 | analog_value | 11018 | seconds | X
rt_fb_row9 | 0 | Frame buffer data for row 9 on the display | H | 8 | 319 | Holding | RW | 408235 408236 | 8234 8235 | REGx2I32 |  |  | rt_fb_row9 | analog_value | 11019 | seconds | X
rt_fb_row10 | 0 | Frame buffer data for row 10 on the display | H | 8 | 322 | Holding | RW | 408237 408238 | 8236 8237 | REGx2I32 |  |  | rt_fb_row10 | analog_value | 11020 | seconds | X
App_EnableMenuFan | 1 | Enable Fan menu page | X | 10 | 0 | Holding | RW | 407001 | 7000 | U8
App_EnableMenuForcedVent | 1 | Enable Forced ventilation menu page | X | 10 | 1 | Holding | RW | 407002 | 7001 | U8
App_EnableMenuHumidity | 1 | Enable Humidity menu page | X | 10 | 2 | Holding | RW | 407003 | 7002 | U8
App_EnableMenuCO2 | 1 | Enable CO2 menu page | X | 10 | 3 | Holding | RW | 407004 | 7003 | U8
App_EnableMenuVOC | 1 | Enable VOC menu page | X | 10 | 4 | Holding | RW | 407005 | 7004 | U8
App_EnableSetpoint | 1 | Enable setpoint setting from display | X | 10 | 5 | Holding | RW | 407006 | 7005 | U8
App_EnableMenuMode | 0 | Enable Mode menu page | X | 10 | 7 | Holding | RW | 407008 | 7007 | U8
App_ModeMenuTitle | MODE | Mode menu title | $ | 10 | 8
App_ModeMenuAutoText | AUTO | Mode menu Auto state text | $ | 10 | 11
App_ModeMenuOffText | OFF | Mode menu Off state text | $ | 10 | 14
App_ModeMenuUnoccText | OFF | Mode menu Unoccupied state text | $ | 10 | 17
App_ModeMenuStandbyText | ECO | Mode menu Standby state text | $ | 10 | 20
App_ModeMenuOccText | ON | Mode menu Occupied state text | $ | 10 | 23
App_ModeMenuBypassText | MAX | Mode menu Bypass state text | $ | 10 | 26
App_ModeMenuOffEnable | 1 | Mode menu Off state enable | L | 10 | 29
App_ModeMenuUnoccEnable | 0 | Mode menu Unoccupied state enable | L | 10 | 30
App_ModeMenuStandbyEnable | 0 | Mode menu Standby state enable | L | 10 | 31
App_ModeMenuOccEnable | 1 | Mode menu Occupied state enable | L | 10 | 32
App_ModeMenuBypassEnable | 0 | Mode menu Bypass state enable | L | 10 | 33
SCD40_ASC_enable | 1 | Enable automatic calibration of CO2 sensor | L | 10 | 50 | Coil | RW | 000101 | 100 | LOGIC
SCD40_ASC_target | 400 | Automatic calibration of CO2 sensor target | I | 10 | 51 | Holding | RW | 400101 | 100 | I16
SCD40_factory_reset | 1 | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset | L | 10 | 53 | Coil | RW | 000102 | 101 | LOGIC
SCD40_FRC_result | 0 | Calculated offset after calibration or -9999 if failed. | I | 10 | 54 | Holding | RW | 400102 | 101 | I16
SCD40_FRC_enable | 0 | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done | L | 10 | 56 | Coil | RW | 000103 | 102 | LOGIC
SCD40_FRC_target | 400 | Current actual CO2 value to calibrate to | I | 10 | 57 | Holding | RW | 400103 | 102 | I16
PLA | 254 |  | X | 241 | 0
ELA | 30 |  | X | 241 | 1
Ver_Minor |  |  | X | 241 | 16 | Input | R | 300007 | 6 | U8
Ver_Major |  |  | X | 241 | 17 | Input | R | 300006 | 5 | U8
MODEL_ALIAS |  | Model number | I | 241 | 36 | Input | R | 300050 | 49 | I16
Model |  | Model number | I | 241 | 36 | Input | R | 300002 | 1 | I16
Ver_Branch |  |  | X | 241 | 40 | Input | R | 300008 | 7 | U8
Ver_Number |  |  | X | 241 | 41 | Input | R | 300009 | 8 | U8
SerialNumberString | 0 |  | $ | 241 | 60
ControllerName | RegioX |  | $ | 241 | 63 | Holding | RW | 400039 - 400070 | 38 - 69 | STRING
ControllerProject | 0 |  | $ | 241 | 66
ControllerDescription |  | Controller description | $ | 241 | 69
ControllerLocation |  | Controller location | $ | 241 | 72
UptimeMillisec | 0 |  | I | 241 | 75
UptimeSec | 0 |  | H | 241 | 77
GitCommit |  | Internal revision number | I | 241 | 80 | Input | R | 300011 | 10 | I16
ModelName | 0 |  | $ | 241 | 100
VendorName | AB Regin |  | $ | 241 | 109
OSid |  | Application OPERATING_SYSTEM_ID | H | 241 | 138
BACnetCommitSettings | 0 | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | RegioX | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | BACnet APDU segment timeout | I | 242 | 69
BACnetWideCharacterSetEncoding | 0 | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetMaxServerCOV | 100 | BACnet max server COV | I | 242 | 135
BACnetPassword | gioP5TJBP8FASqREs6zX | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | Active Modbus unit ID | X | 242 | 172 | Holding | RW | 400002 | 1 | U8
ModbusCharTimeout_Port_1 | 3 |  | I | 242 | 197 | Holding | RW | 400008 | 7 | I16
ModbusAnswerDelay_Port_1 | 5 |  | I | 242 | 199 | Holding | RW | 400009 | 8 | I16
Mode_Port_1 | 2 | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 |  | X | 248 | 38
Baud_Port_1 | 0 | Active RS485 port baud rate | X | 248 | 41
Note on K3: LOGIC: Used for True/False values, only allowed for "Discrete inputs" and "Coils" U8: One 8 bit unsigned integer variable to/from LSB of one register I16: One 16 bit integer variable to/from one register I16SO: Floating point variable converted to 16 bit integer to/from one register. Scale and Offset used REGx2IEEE: First register: MSW of floating point variable to/from one 16-bit register (IEEE) Second register: LSW of floating point variable to/from one 16-bit register (IEEE) REGx2I32: First register: MSW of 32 bit integer variable to/from one 16-bit register Second register: LSW of 32 bit integer variable to/from one 16-bit register REGx2I32SO: First register: MSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O Second register: LSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O
Note on C5: 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on C8: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on O8: 1 = Inactive 3 = EXOline slave 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on C9: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on O9: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on C10: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on O10: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on C16: 0 = Disabled 1 = Set outputs to default values 2 = Set controller state to a default value 3 = Set outputs to default values, start device in offline mode
Note on O16: 1 = Disabled 2 = Set outputs to default values 3 = Set controller state to a default value 4 = Set outputs to default values, start device in offline mode
Note on C20: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C22: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C24: 0 = No faults 1 = Internal Error 2 = Calibration Lost during startup 4 = Calibration memory failed
Note on C33: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on C47: 0 = Off 1 = Green 2 = Yellow 3 = Red
Note on O47: 1 = Off 2 = Green 3 = Yellow 4 = Red
Note on C58: 0 = Fan off 1 = Fan at low speed 2 = Fan at medium speed 3 = Fan at high speed 4 = Fan in Auto mode
Note on O58: 1 = Fan off 2 = Fan at low speed 3 = Fan at medium speed 4 = Fan at high speed 5 = Fan in Auto mode
Note on C67: 0 = Actual temperature 1 = Heat setpoint 2 = Cool setpoint 3 = Average value of heating and cooling setpoint 4 = Setpoint offset 5 = CO2 level 6 = Heat setpoint + offset 7 = Cool setpoint + offset 8 = Average setpoint + offset 9 = Calculated air flow 10 = Active setpoint + offset
Note on O67: 1 = Actual temperature 2 = Heat setpoint 3 = Cool setpoint 4 = Average value of heating and cooling setpoint 5 = Setpoint offset 6 = CO2 level 7 = Heat setpoint + offset 8 = Cool setpoint + offset 9 = Average setpoint + offset 10 = Calculated air flow 11 = Active setpoint + offset
Note on C68: 0 = Setpoint offset 1 = Active setpoint + offset 2 = Heat setpoint + offset 3 = Cool setpoint + offset 4 = Heat occupied setpoint + offset 5 = Cool occupied setpoint + offset 6 = Average setpoint + offset
Note on O68: 1 = Setpoint offset 2 = Active setpoint + offset 3 = Heat setpoint + offset 4 = Cool setpoint + offset 5 = Heat occupied setpoint + offset 6 = Cool occupied setpoint + offset 7 = Average setpoint + offset
Note on C75: 0 = Always off 1 = Show only when the value is displayed 2 = Always on
Note on C77: 0 = Controller mode Off 1 = Controller mode Heating 2 = Controller mode Cooling
Note on C86: 0 = Do not display any boot screen 1 = Display device type 2 = Display device type and model 3 = Display device type, model and version 4 = Display device type, model, version and addresses
Note on C87: 0 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 1 = 5 pixels high font 2 = 7 pixels high font 3 = 10 pixels high font
Note on O87: 1 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 2 = 5 pixels high font 3 = 7 pixels high font 4 = 10 pixels high font
Note on C88: 0 = Show only one row of text 1 = Show two rows of text
Note on O88: 1 = Show only one row of text 2 = Show two rows of text
Note on C89: 0 = Wrap text at the end 1 = Bounce between start and end position 2 = Wrap text at the end, sync row 1 and 2 3 = Bounce between start and end position, sync row 1 and 2
Note on O89: 1 = Wrap text at the end 2 = Bounce between start and end position 3 = Wrap text at the end, sync row 1 and 2 4 = Bounce between start and end position, sync row 1 and 2
Note on C91: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on O91: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on C95: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on O95: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on C108: 0 = Disabled 1 = Enabled 2 = Read only
Note on C109: 0 = Disabled 1 = Enabled 2 = Read only
Note on C110: 0 = Disabled 1 = Enabled 2 = Read only
Note on C111: 0 = Disabled 1 = Enabled 2 = Read only
Note on C112: 0 = Disabled 1 = Enabled 2 = Read only
Note on C113: 0 = Disabled 1 = Enabled 2 = Read only
Note on C114: 0 = Disabled 1 = Enabled 2 = Read only
Note on C172: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on C173: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on C175: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s